## ERI_Prototype 1 PO-PM
ERI_Datum Streams
Performance Aspect
ERI Prototype Scenario | Building Function | Thermal Loads | System Perfomance | Legislation | Energy Consumption | Building Object | Building Object Description (Optional) | Performance Objective | Performance Metric | Benchmark Value | PM Unit | Formula | Note - Open Issues
1 |  | 1 |  |  |  | Site | Weather Conditions | Monitor Temperature | Outside Air Temperature @ LGF level |  | ºC | Datum1
1 |  |  |  |  | 1 | Building |  | Minimise Building Operation Cost | Cost of Operation |  | € | Datum9 * Constant 1 + Datum11 * Constant 7
1 |  |  |  | 1 |  | Building |  | Do not Exceed CO2 emissions threshold | CO2 Emissions |  | kg | Datum9 * Constant 2 + Datum11 * Constant 3
1 |  |  |  |  | 1 | Boiler |  | Minimise Energy Consumption | Gas Consumption |  | m3 | Datum12
1 |  |  |  |  | 1 | Heat Pump |  | Optimise Operation | Electricity Consumption |  | kWh | Datum31
1 |  |  |  |  | 1 | Heat Pump |  | Minimise Cost | Cost of Operation |  | € | Datum31 * Constant 1
1 |  |  |  |  | 1 | Heat Pump |  | Optimise Heat Pump Output | Heat Output |  | kWh | Datum38
1 |  |  | 1 |  |  | Heat Pump |  | Maximise COP | COP |  | - | Datum38 / Datum31
1 |  |  | 1 |  |  | UFH Manifold 0.02 |  | Maintain Intended Supply Temperature | Supply Water Temperature |  | ºC | Datum48
1 |  |  | 1 |  |  | UFH Manifold 1.01 |  | Maintain Intended Supply Temperature | Supply Water Temperature |  | ºC | Datum56
1 |  |  | 1 |  |  | UFH Manifold 1.03 |  | Maintain Intended Supply Temperature | Supply Water Temperature |  | ºC | ºC
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Maintain Themal Comfort | PMV |  | - | F(Datum93 and Datum95 and Datum96 and Constant 4 and Constant 5 and Constant 6)
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Maintain Working Lighting levels | Lux Level |  | Lux | Datum101
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Monitor Air Relative Humidity | Air Relative Humidity |  | % | Datum94
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Maintain Air Temperature Setpoint | Air Temperature |  | ºC | Datum93
1 | 1 |  |  |  |  | G05: Immunology Lab | Door Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum102
1 | 1 |  |  |  |  | G05: Immunology Lab | Wooden Opening 1 (West) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum103
1 | 1 |  |  |  |  | G05: Immunology Lab | Wooden Opening 2 (East) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum104
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Monitor Zone Occupancy | CO2 Level |  | PPM | Datum98
1 | 1 |  |  |  |  | G05: Immunology Lab |  | Monitor Zone Occupancy | PIR |  | - | Datum97
1 |  | 1 |  |  | 1 | G05: Immunology Lab |  | Minimise Lighting Thermal Load | Lighting Electricity |  | kWh | Datum99
1 |  | 1 |  |  | 1 | G05: Immunology Lab |  | Minimize Plug Thermal Loads | Plug Load Electricity |  | kWh | Datum100
1 |  | 1 |  |  |  | G05: Immunology Lab |  | Monitor Occupancy Thermal Load | Occupancy Thermal Load |  | kWh | F(Datum97 and Datum98)
1 |  |  |  |  | 1 | G05: Immunology Lab |  | Minimise Zone Heating Energy | Heating Energy |  | kWh | Datum52 * Constant 8 * Constant 9 ( Datum48 - Datum50 ) + Datum55 * Constant 8 * Constant 9 ( Datum48 - Datum53 )
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Maintain Themal Comfort | PMV |  | - | F(Datum105 and Datum107 and Datum108 and Datum109 and Datum110 and Constant 4 and Constant 5 and Constant 6)
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Maintain Working Lighting levels | Lux Level |  | Lux | F(Datum117 and Datum118)
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Monitor Air Relative Humidity | Air Relative Humidity |  | % | Datum106
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Maintain Air Temperature Setpoint | Air Temperature |  | ºC | Datum105
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Wooden Opening 1 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum121
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Wooden Opening 2 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum122
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Wooden Opening 3 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum123
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Wooden Opening 4 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum124
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Wooden Opening 5 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum125
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Manual Window 1 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum126
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Manual Window 2 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum127
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Manual Window 3 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum128
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Manual Window 4 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum129
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Manual Window 5 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum130
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Automatic Window 1 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum131
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 | Automatic Window 2 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum132
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Monitor Zone Occupancy | CO2 Level |  | PPM | F(Datum113 and Datum114)
1 | 1 |  |  |  |  | 1.23:open plan office right 3.6 |  | Monitor Zone Occupancy | PIR |  | - | F(Datum111 and Datum112)
1 |  | 1 |  |  | 1 | 1.23:open plan office right 3.6 |  | Minimise Lighting Thermal Load | Lighting Electricity |  | kWh | Datum115
1 |  | 1 |  |  | 1 | 1.23:open plan office right 3.6 |  | Minimize Plug Thermal Loads | Plug Load Electricity |  | kWh | Datum116
1 |  | 1 |  |  |  | 1.23:open plan office right 3.6 |  | Monitor Occupancy Thermal Load | Occupancy Thermal Load |  | kWh | F(Datum111 and Datum112 and Datum113 and Datum114)
1 |  |  |  |  | 1 | 1.23:open plan office right 3.6 |  | Minimise Zone Heating Energy | Heating Energy |  | kWh | Datum83 * Constant 8 * Constant 9 ( Datum79 - Datum81 ) + Datum86 * Constant 8 * Constant 9 ( Datum79 - Datum84 ) + Datum89 * Constant 8 * Constant 9 ( Datum79 - Datum87 ) + Datum92 * Constant 8 * Constant 9 ( Datum79 - Datum90 ) | The concatenate function doesn't work for the whole formula, 2 partial formulas are stored here on the right and assemleb in the cell of the formula here on the left) | Datum83 * Constant 8 * Constant 9 ( Datum79 - Datum81 ) + Datum86 * Constant 8 * Constant 9 ( Datum79 - Datum84 ) | + Datum89 * Constant 8 * Constant 9 ( Datum79 - Datum87 ) + Datum92 * Constant 8 * Constant 9 ( Datum79 - Datum90 )
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Maintain Themal Comfort | PMV |  | - | F(Datum133 and Datum135 and Datum136 and Datum137 and Datum138 and Constant 4 and Constant 5 and Constant 6)
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Maintain Working Lighting levels | Lux Level |  | Lux | F(Datum145 and Datum146)
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Monitor Air Relative Humidity | Air Relative Humidity |  | % | Datum134
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Maintain Air Temperature Setpoint | Air Temperature |  | ºC | Datum133
1 | 1 |  |  |  |  | 1.28:Seminar Room | Door Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum147
1 | 1 |  |  |  |  | 1.28:Seminar Room | Sliding Door Open Signal | Monitor Window Door Opening | Opening Signal |  | % | F(Datum146 and Datum147 and Datum148)
1 | 1 |  |  |  |  | 1.28:Seminar Room | Window 1 Open Signal | Monitor Window Door Opening | Opening Signal |  | % | F(Datum147 and Datum148 and Datum149)
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Monitor Zone Occupancy | CO2 Level |  | PPM | F(Datum140 and Datum142)
1 | 1 |  |  |  |  | 1.28:Seminar Room |  | Monitor Zone Occupancy | PIR |  | - | F(Datum139 and Datum141)
1 |  | 1 |  |  | 1 | 1.28:Seminar Room |  | Minimise Lighting Thermal Load | Lighting Electricity |  | kWh | Datum143
1 |  | 1 |  |  | 1 | 1.28:Seminar Room |  | Minimize Plug Thermal Loads | Plug Load Electricity |  | kWh | Datum144
1 |  | 1 |  |  |  | 1.28:Seminar Room |  | Monitor Occupancy Thermal Load | Occupancy Thermal Load |  | kWh | F(Datum139 and Datum140 and Datum141 and Datum142)
1 |  |  |  |  | 1 | 1.28:Seminar Room |  | Minimise Zone Heating Energy | Heating Energy |  | kWh | Datum60 * Constant 8 * Constant 9 ( Datum56 - Datum58 ) + Datum63 * Constant 8 * Constant 9 ( Datum56 - Datum61 ) + Datum66 * Constant 8 * Constant 9 ( Datum56 - Datum65 ) + Datum69 * Constant 8 * Constant 9 ( Datum56 - Datum67 ) | The concatenate function doesn't work for the whole formula, 2 partial formulas are stored here on the right and assemleb in the cell of the formula here on the left) | Datum60 * Constant 8 * Constant 9 ( Datum56 - Datum58 ) + Datum63 * Constant 8 * Constant 9 ( Datum56 - Datum61 ) | + Datum66 * Constant 8 * Constant 9 ( Datum56 - Datum65 ) + Datum69 * Constant 8 * Constant 9 ( Datum56 - Datum67 )
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Maintain Themal Comfort | PMV |  | - | F(Datum150 and Datum152 and Datum153 and Datum154 and Constant 4 and Constant 5 and Constant 6)
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Maintain Working Lighting levels | Lux Level |  | Lux | Datum159
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Monitor Air Relative Humidity | Air Relative Humidity |  | % | Datum151
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Maintain Air Temperature Setpoint | Air Temperature |  | ºC | Datum150
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Windows 1, 2, 3 and 4 Open Signal (opening together) | Monitor Window Door Opening | Opening Signal |  | % | Datum160
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Door 1 (Corridor South) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum161
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Door 2 (Corridor North) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum162
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Door 3 (Kitchen) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum163
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Door 4 (Director Room) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum164
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space | Door 5 (Stair case) Open Signal | Monitor Window Door Opening | Opening Signal |  | % | Datum165
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Monitor Zone Occupancy | CO2 Level |  | PPM | Datum156
1 | 1 |  |  |  |  | 1.28:Seminar Room - Break Out Space |  | Monitor Zone Occupancy | PIR |  | - | Datum155
1 |  | 1 |  |  | 1 | 1.28:Seminar Room - Break Out Space |  | Minimise Lighting Thermal Load | Lighting Electricity |  | kWh | Datum157
1 |  | 1 |  |  | 1 | 1.28:Seminar Room - Break Out Space |  | Minimize Plug Thermal Loads | Plug Load Electricity |  | kWh | Datum158
1 |  | 1 |  |  |  | 1.28:Seminar Room - Break Out Space |  | Monitor Occupancy Thermal Load | Occupancy Thermal Load |  | kWh | F(Datum155 and Datum156)
1 |  |  |  |  | 1 | 1.28:Seminar Room - Break Out Space |  | Minimise Zone Heating Energy | Heating Energy |  | kWh | Datum72 * Constant 8 * Constant 9 ( Datum56 - Datum70 ) + Datum75 * Constant 8 * Constant 9 ( Datum56 - Datum73 ) + Datum78 * Constant 8 * Constant 9 ( Datum56 - Datum76 ) |  | Datum72 * Constant 8 * Constant 9 ( Datum56 - Datum70 ) + Datum75 * Constant 8 * Constant 9 ( Datum56 - Datum73 ) | + Datum78 * Constant 8 * Constant 9 ( Datum56 - Datum76 )
Notes:
Decide how if and how to average Lighting Level, CO2 and PIR measurements
Thew PO qualifiers are intended as guidelines for the user rather than algoritmn followed by the computer
Decide if the PMV metric is appropriate for this spaces with natural ventilation
Define function for occupancy thermal loads
Note on A1: Andrea Costa: Not clear what to assign to : - System Performance -Energy Consumption Can one PO be assigned to 2 different aspects? All the PO are monitor… for now, they could also be maintain, minimise, maximise but in this case a benchmark value is required
Note on L3: Andrea Costa: All the units are intneded per minute. They can be easily intagrated per the time frame selected by the user Only the flow readings and electricity are cumulative values whitin the interval, the other readings are spot measurements taken once per minute. This means that for a 1 minute interval, we'd have m3 per minutes and alike kWh per minute

## ERI_Prototype 1 Datum Streams
ERI_Datum Streams
Building Object | Measurement Description | Datum Stream Name | Datum Stream Unit | Existing | Vitual Datum Stream | Required Wireless Datum Stream | Tier 1 | Tier 2 | Tier 3 | Existing Tier 1 | Existing Tier 2 | Existing Tier 3 | Missing Tier 1 | Missing Tier 2 | Missing Tier 3 | Prototype 1 | Prototype 2 | BMS Output (*.csv file name) | MC -Master Controller | FC -Field Controller | SN -Sensor Number | Desired Measurement Interval | Actual Measurement Interval | Comment
Site | Outside Air Temperature @ LGF level | Datum1 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 1 | 1 | 1
Site | Outside Air Temperature @ roof level | Datum2 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 6 | 3
Site | Outside Wind Direction | Datum3 | degrees |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 2 | 6 | 2
Site | Outside Wind Speed | Datum4 | m/s | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 6 | 1
Site | Outside Air Relative Humidity | Datum5 | % | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Site | Outside Natural Lighting Level | Datum6 | Lux | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Site | Outside Total Solar Radiation | Datum7 | W/m2 | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Site | Outside Diffuse Solar Radiation | Datum8 | W/m2 | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Building | Electricity Total Consumption | Datum9 | kWh | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Building | Lighting Electricity Total Consumption | Datum10 | kWh |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1
Building | Gas Total Consumption | Datum11 | m3 | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Building | Boiler Gas Total Consumption | Datum12 | m3 | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Building | Laboratories Gas Total Consumption | Datum13 | m3 | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Building | Mains Water Supply Total | Datum14 | m3 | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Building | Domestic Hot Water Total | Datum15 | m3 |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1
Building | Cold Water Total | Datum16 | m3 |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1
Aquifer Loop (2-30ºC) | Aquifer Inlet Water Temperature (A1) | Datum17 | ºC | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Mixed HE-01 & HE-02 Outlet Water Temperature (A2) | Datum18 | ºC | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Heat Pump Evaporator Side Outlet Water Temperature (A3) | Datum19 | ºC | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Aquifer Loop Outlet Water Flow | Datum20 | m3 |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1
Aquifer Loop (2-30ºC) | Valve between HE-01 & HE02 Opening (VA1) | Datum21 | % | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Bypass Valve Heat Pump Evaporator Side Loop Opening (VA2) | Datum22 | % | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Valve Heat Pump Evaporator Side Inlet Compressor 1 Opening (VA3) | Datum23 | % | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Aquifer Loop (2-30ºC) | Valve Heat Pump Evaporator Side Inlet Compressor 2 Opening (VA4) | Datum24 | % | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Pump P01 | Electricity Power Consumption | Datum25 | kWh |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P01 | Signal Control | Datum26 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P02 | Electricity Power Consumption | Datum27 | kWh |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P02 | Signal Control | Datum28 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P03 | Electricity Power Consumption | Datum29 | kWh |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P03 | Signal Control | Datum30 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Heat Pump | Electricity Power Consumption | Datum31 | kWh | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Heat Pump | Signal Control | Datum32 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Heat Pump Condenser Side Outlet Water Temperature (UF1) | Datum33 | ºC | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Heat Pump Condenser Side Inlet Water Temperature (UF2) | Datum34 | ºC | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Underfloor Heating Loop Return Supply Water Temperature (UF3) | Datum35 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | HE-04 Outlet - Underfloor Heating Supply Water Temperature (UF4) | Datum36 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Bypass Valve Heat Pump Condenser Side Loop Opening (VUF1) | Datum37 | % | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Heat Pump Condenser Side Loop Heat Meter (HMUF1) | Datum38 | kWh | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Underfloor Heating Loop (20-45ºC) | Underfloor Heating Loop Heat Meter (HMUF2) | Datum39 | kWh | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P8A | Electricity Power Consumption | Datum40 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P8A | Signal Control | Datum41 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P8B | Electricity Power Consumption | Datum42 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P8B | Signal Control | Datum43 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P14A | Electricity Power Consumption | Datum44 | kWh |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P14A | Signal Control | Datum45 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
Pump P14B | Electricity Power Consumption | Datum46 | kWh |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Pump P14B | Signal Control | Datum47 | - | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1
UFH Manifold 0.02 | UFH Manifold 0.02 Supply Water Temperature | Datum48 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 0.02 | Supply Water Flow | Datum49 | m3 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 0.02 - Loop 1 (G05:immunology) | Return Water Temperature | Datum50 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 0.02 - Loop 1 (G05:immunology) | Valve Signal Control | Datum51 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 0.02 - Loop 1 (G05:immunology) | Loop Water Flow | Datum52 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 0.02 - Loop 2 (G05:immunology) | Return Water Temperature | Datum53 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 0.02 - Loop 2 (G05:immunology) | Valve Signal Control | Datum54 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 0.02 - Loop 2 (G05:immunology) | Loop Water Flow | Datum55 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 | UFH Manifold 1.03 Supply Water Temperature | Datum56 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 | Supply Water Flow | Datum57 | m3 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 1 (1.28 Seminar Room 3.16) | Return Water Temperature | Datum58 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 1 (1.28 Seminar Room 3.16) | Valve Signal Control | Datum59 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 1 (1.28 Seminar Room 3.16) | Loop Water Flow | Datum60 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 2 (1.28 Seminar Room 3.16) | Return Water Temperature | Datum61 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 2 (1.28 Seminar Room 3.16) | Valve Signal Control | Datum62 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 2 (1.28 Seminar Room 3.16) | Loop Water Flow | Datum63 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 3 (1.28 Seminar Room 3.16) | Return Water Temperature | Datum64 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 3 (1.28 Seminar Room 3.16) | Valve Signal Control | Datum65 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 3 (1.28 Seminar Room 3.16) | Loop Water Flow | Datum66 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 4 (1.28 Seminar Room 3.16) | Return Water Temperature | Datum67 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 4 (1.28 Seminar Room 3.16) | Valve Signal Control | Datum68 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 4 (1.28 Seminar Room 3.16) | Loop Water Flow | Datum69 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 5 (1.28:Seminar Room - Break Out Space) | Return Water Temperature | Datum70 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 5 (1.28:Seminar Room - Break Out Space) | Valve Signal Control | Datum71 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 5 (1.28:Seminar Room - Break Out Space) | Loop Water Flow | Datum72 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 6 (1.28:Seminar Room - Break Out Space) | Return Water Temperature | Datum73 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 6 (1.28:Seminar Room - Break Out Space) | Valve Signal Control | Datum74 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 6 (1.28:Seminar Room - Break Out Space) | Loop Water Flow | Datum75 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 7 (1.28:Seminar Room - Break Out Space) | Return Water Temperature | Datum76 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.01 - Loop 7 (1.28:Seminar Room - Break Out Space) | Valve Signal Control | Datum77 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.01 - Loop 7 (1.28:Seminar Room - Break Out Space) | Loop Water Flow | Datum78 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 | UFH Manifold 1.03 Supply Water Temperature | Datum79 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 | Supply Water Flow | Datum80 | m3 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 10 (1.23 Open Plan Office 3.6) | Return Water Temperature | Datum81 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 10 (1.23 Open Plan Office 3.6) | Valve Signal Control | Datum82 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.03 - Loop 10 (1.23 Open Plan Office 3.6) | Loop Water Flow | Datum83 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 11 (1.23 Open Plan Office 3.6). | Return Water Temperature | Datum84 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 11 (1.23 Open Plan Office 3.6) | Valve Signal Control | Datum85 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.03 - Loop 11 (1.23 Open Plan Office 3.6) | Loop Water Flow | Datum86 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 12 (1.23 Open Plan Office 3.6) | Return Water Temperature | Datum87 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 12 (1.23 Open Plan Office 3.6) | Valve Signal Control | Datum88 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.03 - Loop 12 (1.23 Open Plan Office 3.6) | Loop Water Flow | Datum89 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 13 (1.23 Open Plan Office 3.6) | Return Water Temperature | Datum90 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
UFH Manifold 1.03 - Loop 13 (1.23 Open Plan Office 3.6) | Valve Signal Control | Datum91 | Open/Close | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
UFH Manifold 1.03 - Loop 13 (1.23 Open Plan Office 3.6) | Loop Water Flow | Datum92 | m3 |  | 1 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
G05: Immunology Lab | Air Temperature | Datum93 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Air Relative Humidity | Datum94 | % RH | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Radiant Temperature (UFH Loop1) | Datum95 | ºC | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Radiant Temperature (UFH Loop2) | Datum96 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Occupancy - PIR | Datum97 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Occupancy - CO2 | Datum98 | PPM | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Lighting Electricity | Datum99 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Plug Load Electricity | Datum100 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Lighting Level | Datum101 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Door Open Signal | Datum102 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Wooden Opening 1 (West) Open Signal | Datum103 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
G05: Immunology Lab | Wooden Opening 2 (East) Open Signal | Datum104 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Air Temperature | Datum105 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Air Relative Humidity | Datum106 | % | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Radiant Temperature (UFH Loop 10) | Datum107 | ºC | 1 |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Radiant Temperature (UFH Loop 11) | Datum108 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Radiant Temperature (UFH Loop 12) | Datum109 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Radiant Temperature (UFH Loop 13) | Datum110 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Occupancy East - PIR | Datum111 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Occupancy West - PIR | Datum112 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Occupancy East - CO2 | Datum113 | PPM | 1 |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Occupancy West - CO2 | Datum114 | PPM |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Lighting Electricity | Datum115 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Plug Load Electricity | Datum116 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Lighting Level East | Datum117 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Lighting Level West | Datum118 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Door 1 (West) Open Signal | Datum119 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Door 2 (East) Open Signal | Datum120 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Wooden Opening 1 Open Signal | Datum121 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Wooden Opening 2 Open Signal | Datum122 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Wooden Opening 3 Open Signal | Datum123 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Wooden Opening 4 Open Signal | Datum124 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Wooden Opening 5 Open Signal | Datum125 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Manual Window 1 Open Signal | Datum126 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Manual Window 2 Open Signal | Datum127 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Manual Window 3 Open Signal | Datum128 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Manual Window 4 Open Signal | Datum129 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Manual Window 5 Open Signal | Datum130 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Automatic Window 1 Open Signal | Datum131 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.23:open plan office right 3.6 | Automatic Window 2 Open Signal | Datum132 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Air Temperature | Datum133 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Air Relative Humidity | Datum134 | % RH |  |  | 1 | 1 |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Radiant Temperature (UFH Loop 1) | Datum135 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Radiant Temperature (UFH Loop 2) | Datum136 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Radiant Temperature (UFH Loop 3) | Datum137 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Radiant Temperature (UFH Loop 4) | Datum138 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Occupancy East - PIR | Datum139 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Occupancy East - CO2 | Datum140 | PPM |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Occupancy West - PIR | Datum141 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Occupancy West - CO2 | Datum142 | PPM |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Lighting Electricity | Datum143 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Plug Load Electricity | Datum144 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Lighting Level East | Datum145 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Lighting Level West | Datum146 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Door Open Signal | Datum147 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Sliding Door Open Signal | Datum148 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room | Window 1 Open Signal | Datum149 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Air Temperature | Datum150 | ºC | 1 |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Air Relative Humidity | Datum151 | % RH |  |  | 1 | 1 |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Radiant Temperature (UFH Loop 5) | Datum152 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Radiant Temperature (UFH Loop 6) | Datum153 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Radiant Temperature (UFH Loop 7) | Datum154 | ºC |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Occupancy - PIR | Datum155 | - |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Occupancy - CO2 | Datum156 | PPM |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Lighting Electricity | Datum157 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Plug Load Electricity | Datum158 | kWh |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Lighting Level | Datum159 | Lux |  |  | 1 |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Windows 1, 2, 3 and 4 Open Signal (opening together) | Datum160 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Door 1 (Corridor South) Open Signal | Datum161 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Door 2 (Corridor North) Open Signal | Datum162 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Door 3 (Kitchen) Open Signal | Datum163 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Door 4 (Director Room) Open Signal | Datum164 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
1.28:Seminar Room - Break Out Space | Door 5 (Stair case) Open Signal | Datum165 | % |  |  | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | 15 Minutes
Note on D2: Andrea Costa: Only the flow readings and electricity are cumulative values whitin the interval, the other readings are spot measurements taken once per minute. This needs further investigation on sensors/meters and what values are needed.

## Constant Values
Constant Name | Constant Description | Constant Value | Constant Unit
Constant 1 | Electricity unit cost | 0.05 | €/kWh
Constant 2 | kg of CO2 per kWh of Gasy consumed | 0.0055 | kg/kWh
Constant 3 | kg of CO2 per kWh of Electricity consumed | 0.194 | kg/kWh
Constant 4 | Metabolism |  | met
Constant 5 | Clothing |  | m2K/W
Constant 6 | Air Velocity |  | m/s
Constant 7 | Gas unit cost |  | €/m3
Constant 8 | Water Specific Heat | 4.2 | kJ/(kg*K)
Constant 9 | Water Density | 1000 | kg/m3
Note on C1: Andrea Costa: Approx Value