## EnergyManager_View
Building Objects | Measurements Required | Unit | Interval | Energy Manager | Accountant | Tier 1 | Tier 2 | Tier 3 | Performance Objective | Performance Metric and Unit | Resolution | Description of Measurements | Comment
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14
Site | Outdoor DB Temp sensor | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Monitor Outdoor DB Temp | Outdoor Dry Bulb Temp (oC) |  | This measurement stream is the most important indicator of the nature of external conditions. This datum stream can be used to determine degree days and to understand the time lag between external temperatures and its effect on indoor environmental conditions. It can also and important measurement stream when optimizing economizer operation | North Façade in permanent shade
Site | South Façade Outdoor DB Temp sensor | oC | 1 Minute | 1 |  | 1 | 1 | 1
Site | East Façade Outdoor DB Temp sensor | oC | 1 Minute | 1 |  | 1 | 1 | 1
Site | West Façade Outdoor DB Temp sensor | oC | 1 Minute | 1 |  | 1 | 1 | 1
Site | Outdoor WB Temp sensor | oC | 1 Minute | [5 empty] | Monitor Outdoor WB Temp | Outdoor Wet Bulb Temp (oC) |  | If this stream is missing, it is impossible to establish a link between external environmental conditions and zone conditions. | Either Wet Bulb or RH
Site | or OA Humididy | % | 1 Minute | 1 |  | 1 |  | 1 | Moitor Outdoor % Humidity | Outdoor Humidity (%) |  | This measurement stream can give an indication if supply air requires humidification. It can also be used for enthalpy based control of mixing boxes. If this stream is absent poor indoor environmental conditions may result.
Site | [8 empty] | Monitor Average Daily DB Temp | Average Daily Outdoor Temp (oC)
Site | Wind Velocity | m/s | 1 Minute | 1 |  |  | 1 | 1 | Monitor Heating Degree Days | Heating Degree Days (Dimensionless) |  | These measurement streams are vital in situations where natural ventilation is used. Independently high wind speeds can have a heating/cooling effect on a building. Extremely high wind speeds may also trigger an alarm to close all windows
Site | Wind Direction | Degrees | 1 Minute | 1 |  |  |  | 1 | Monitor Cooling Degree Days | Heating Degree Days (Dimensionless)
Site | Solar Radiation | kWh | 1 Minute | 1 |  | 1 |  | 1 | Monitor Wind Speed | Wind Speed (m/s) |  | This datum stream is used to determine the amount of solar radiation falling on a building. It is an essential measurement where PV and solar thermal systems are installed. Solar radiation can also be closely coupled with cooling electrical load.
[9 empty] | Monitor Wind Direction | Wind Direction (Degrees) |  | If the solar radiation measurement stream is absent, then it is impossible to quantify the effect solar radiation has on building performance.
| Outdoor Natural Light Levels | Lux | 1 Minute | 1 |  | 1 | 1 | 1 | Monitor Total Incident Solar | Total Incident Solar Radiation (kWh) |  | Outdoor natural light levels are a useful measurement where day-lighting strategies are in place. It quantifies available natural light that should act as a reference for natural light levels that are available indoors. This Lux measurement can also be used for the automated control of external lighting. If lighting is manually controlled it has the potential to consume more energy than is required.
| Night Sky Radiant Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Monitor Available Natural Night | Available Natural Light (Lux) |  | This measurement is necessary for buildings that incorporate night sky cooling systems. It gives an indicator of the cooling potential on any particular night.
If this measurement is missing operational performance of the cooling system can not be determined.
Building | Building Occupancy Level (Office Building) | People | 1 Minute | 1 | 1 | 1 | 1 | 1 |  |  |  | The purpose of this measurement is to define building function. This measurement (e.g. building occupancy level, units produced etc.) enables a comparison of organizational performance and energy consumption. Without this measurement stream it is difficult to make a fair comparison. If for example more people occupy a building in year 2 compare with year 1 it is highly probably that extra energy will be consumed in year 2 when compared with year 1.
Building | Building Function (Units produced) | Units | 1 Minute | 1 | 1
Building | Occupant Satisfaction |  |  | 1
Building | Floor Area (m2) | m2 | 1 Minute | 1 | 1 | 1 | 1 | 1
Building | Building Volume (m3) | m3 | 1 Minute | 1 | 1 | 1 | 1 | 1
Primary Energy Use
Building | Utility Bills (Monthly Monetary Values) | Euro | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Building Energy Use | Total Energy Use (kWh) |  | Utility bills are used by financial controllers. Cost and energy consumption (kWh or m3) values are the key parameters. A calorific value is required to convert gas volumes of gas into kWh energy values. Without these measurement streams communication between the energy manager and financial controller is extremely difficult. | Duplicate refer to energy by utility
Building | Utility Energy Consumption | kWh/M2/Year | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Builidng EUI | EUI (kWh/M2/Year) |  | The first level of understanding energy consumption can come from analyzing monthly energy consumption. E.g. is a higher electrical load in summer a result of additional cooling? 10 minute pricing information is critical where dynamic tariffs are used. If building area or building volume is used then an informative EUI can be established for a building.
Building | Utility Energy Consumption, Volume | m3 | 1 Minute | 1 | 1 |  |  | 1 | Minimise Builidng EUI | EUI (kWh/M3/Year) |  | Also an increase in Gas consumption would normally be expected in winter.
Building | Utility Bills (10 minute price information) | Euro | 1 Minute | 1 | 1 |  |  | 1 | Minimise Total Energy Cost | Total Energy Cost (Unit of Local Currency) |  | If the resolution of measurement is reduced from monthly to a sub hourly time step a clearer picture of the operational characteristics of the building emerge. Start up times for the building can become clear. An energy manager can visualize the time at which peak electrical power occurs. A night time electrical baseline can be established. Initial understanding of gas consumption can be based on sub hourly readings. Again base lines and heating periods can be established (The same measurements and principles apply for oil and water use).
Building | Utiltiy bills (Monthly Consumption Values) | CO2 | 1 Minute | 1 | 1 |  |  | 1 | Normalized atmospheric emissions | Tons CO2
Building | Elec & Gas Total/(Area Conditioned) | kWh/M2/Year | 1 Minute | 1 |  | 1 |  | 1 | Minimise HVAC Energy Cost | Total HVAC Cost (Unit of Local Currency)
[9 empty] | Minimise HVAC Energy use | Total HVAC EUI (kWh/M2/Year)
Electricty
Building | Electricity Bills (Cost) | Euro | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Electricity Use | Tolal Electrical Consumption (kWh)
Building | Electricity Energy Consumption | kWh | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise peak power required | Whole Building Peak Power (kWh)
Building | Building Volume | m3 | 1 Minute | 1 |  | 1 | 1 | 1 | Normalised Electricty Consumption | Electricty Consumption (kWh/Time Period)
Building | Electricity Bills (10 minute price information) | Euro | 1 Minute | 1 |  |  | 1 | 1 | Electrical EUI | Electrical EUI (kWh/M2/Year)
Building | Sum HVAC Elec Sub meters | kWh | 1 Minute | 1 |  |  | 1 | 1 | Electrical Cost | Electrical Cost (Unit of Local Currency)
[9 empty] | Minimise Electricity use | Average Daily Electrical Power (kWh)
[9 empty] | Minimise electrical CO2 emissions | Electricty Related CO2 Emissions (kgC02/kWh)
[9 empty] | Minimise hvac peak power | Total HVAC Electric Power (kW)
[9 empty] | Minimise HVAC Elec Energy Use | Whole Building HVAC Electrical EUI (kWh/M2)
Gas
Building | Gas Meter or Utilty Bill | m3 | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Gas Consumption | Total Gas Use (kWh)
Building | Utility Bills (Gas Cost) | Euro | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Peak Gas Load | Building Peak Gas Load (kWh)
Building | Gas Calorific Value | kW | 1 Minute | [5 empty] | Minimise Gas Energy Use | Normalised Gas Consumption (kWh/Time Period)
Building | Sum of HVAC Gas Meters | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise Gas energy use intensity | Gas EUI (kWh/M2)
[9 empty] | Minimise Gas Cost | Gas Cost (Unit of Local Currency)
[9 empty] | Minimise HVAC Gas Energy Use Intensity | HVAC Gas EUI (kWh/M2)
[9 empty] | Minimise Gas HVAC Consumption | Total HVAC heater Gas Flow (kWh)
[9 empty] | Minimise Daily Gas Consumption | Daily Total Gas flow (kWh)
[9 empty] | Minimise Gas related CO2 emissions | Gas related CO2 emissions
Oil
Building | Oil Meter(M3) or Utilty Bill | m3 | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Oil Consumption | Total Oil USe (kWh)
Building | Utility Bills (Oil Cost) | kWh | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Peak oil use | Building Peak Oil (kWh)
Building | Sum of HVAC Oil Meters | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise oil Consumption | Normalised Oil Consumption (kWh/Time Period)
[9 empty] | Minimise oil EUI | Oil EUI (kWh/M2)
[9 empty] | Minimise oil Cost | Oil Cost (Unit of Local Currency)
[9 empty] | Minimise HVAC oil Consumption | HVAC Oil EUI (kWh/M2)
[9 empty] | Minimise Daily Oil Consumption | Daily Total Oil Use (kWh)
[9 empty] | Minimise Oil related CO2 emissions | Oil related CO2 emissions (kgC02/kWh)
Water
Building | Water Meter | m3 | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise Peak Water Consumption | Building Peak Water (M3)
Building | Utiltiy Bill (Cost) | Euro | 1 Minute | 1 | 1 | 1 | 1 | 1 | Minimise water consumption | Normalised Water Consumption (M3)
Building | Sum of Individual Water Meters | m3 | 1 Minute |  |  |  | 1 |  | Minimise water Use Intensity | Water UI (M3/M2)
[9 empty] | Minimise Water Cost | Water Cost
Cooling
Building | Total Electrical Plant Cooling | kW | 1 Minute | 1 |  | 1 | 1 | 1 | Minimise Peak Elec Cooling Load | Peak Elec Cooling Load (kW) |  | Using these categories, a comprehensive understanding of performance can be established. If sub hourly measurements are taken for these categories then a further level of understanding can be attained.
Building | Chilled Plant Supply Temp | oC | 1 Minute | [5 empty] | Minimise Elec Cooling Load | Normalised Elec Cooling Load (kWh/time period) |  | Without this type of breakdown, it may be impossible for a building manager to establish where energy is consumed. Baseline energy consumption values could be established for each criterion and compared with normal operating energy consumption values. | Dupllicate Measurement Refer to chiller
Building | Chillers Return Temp | oC | 1 Minute | [5 empty] | Minimise Chilled Water Output | Generated Cooling (kWh) |  |  | Duplicate meaurement refer to chiller
Building | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1 |  |  |  |  | Dupllicate Measurement Refer to chiller
Building | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Building | Chilled Plant Flow rate | m3 | 1 Minute | [5 empty] | Maximise Chilled Plant Efficiency | All Chillers Efficiency (%) |  | Further breakdown of cooling energy consumed would require meters for the chillers total electricity and for the total cooling towers/condensers electricity. These readings would enable further understanding of operational characteristics. | Dupllicate Measurement Refer to chiller
Building | Chiller water pumps elec | kWh | 1 Minute | [5 empty] | Minimmise Cooling Load EUI | Minimise Cooling EUI (kWh/M2/Year) |  |  | Dupllicate Measurement Refer to chiller
Building | Cooling Towers Elec | kWh | 1 Minute | [5 empty] | Minimmise Cooling Load EUI | Minimise Cooling EUI (kWh/M3/Year) |  |  | Dupllicate Measurement Refer to Cooling Tower
[9 empty] | Monitor Chilled Water Delta T | Chilled Water Loop Delta T (oC)
[9 empty] | Average Chilled Water Supply Temp | Average Daily Chilled water Supply Temp (oC)
[9 empty] | Minimise Daily Chilled Plant Elec | Daily Chilled Water Plant Electric usage (kWh)
[9 empty] | Monitor Chilled Plant Daily Output | Daily Chilled Water Plant Output (kWh)
[9 empty] | Minimise Time of Max Chilled Water Output | Maximum Time period chilled water output (Minutes)
[9 empty] | Maximise Daily Chilled Efficiency | Average Daily Chilled water efficiency (%)
[9 empty] | Monitor Cold Storage Energy Used | Cold Storage Energy Transfer (kWh)
[9 empty] | Minimise Chilled plant Rejected Heat | Total Chilled Water Plant Heat Rejection (kWh)
Heating
Building | Sum Gas (Boilers) | m3 | 1 Minute | [5 empty] | Minimise Heating Load (Supply & Demand) | Heating Load (kWh & M3) |  | Further breakdown of the heating energy consumed would require meters for the total boilers gas consumption and the total for electrical heating. These readings would enable further understanding of operational characteristics. | Duplicate measurement refer to Heating System
Building | Heating System flow rate | m3 | 1 Minute | [5 empty] | Minimise Peak Heating Load | Peak Heating Load (kWh & M3) |  |  | Duplicate measurement refer to Heating System
Building | Heating System Supply Temp | oC | 1 Minute | [5 empty] | Maximise Heating Plant Efficiency | Boilers Efficiency (%) |  |  | Duplicate measurement refer to Heating System
Building | Heating System Ret Temp | oC | 1 Minute | [5 empty] | Minimise Heating Load EUI (Area) | Minimise Heating EUI (kWh/M2Area Heated/Year) |  |  | Duplicate measurement refer to Heating System
Building | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1 |  |  |  |  | Duplicate measurement refer to Heating System
Building | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1 |  |  |  |  | Duplicate measurement refer to Heating System
Building | Building Area Heated | m2 | 1 Minute | 1 |  |  | 1 | 1 | Minimise Heating Load EUI (Vol) | Minimise Heating EUI (kWh/M3Volume Heated/Year)
Building | Total Electrical Heating | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise Daily Heating Energy Use | Daily Total Heating Energy Use (kWh)
Lighting
Building | Sum Lighting Sub Meters | kWh | 1 Minute | 1 |  |  |  | 1 | Maximise Lighting Efficiency | Lighting Efficiency (Lux/Watt) |  | Further breakdown of the lighting energy consumed would require meters for the total zone lighting load, total outdoor lighting load and total electrical lighting load. These readings would establish if outdoor lighting is running during the day and if zone lighting was being used when the building is not occupied.
Building | Sum Zone Lighting Meters | kWh/M2/Year | 1 Minute | 1 |  |  |  | 1 | Minimise Lighting EUI | Lighting EUI (kWh/M2/Year)
Building | Outdoor Lighing Sensor | Lux | 1 Minute | [5 empty] | Minimise Lighting Energy Use | Lighting Energy Use (kWh) |  |  | Duplicate measurement refer to Site
Building | Emergency Lighting Elec Meter | kWh | 1 Minute | 1 |  |  | 1 | 1
Ventilation
Building | Sum Systems Cumulative Flow Rate | m3 | 1 Minute | 1 |  |  | 1 | 1 | Minimise Air Flow | Total AHUs Air Flow (M3) |  | Total Ventilation electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Building | Sum AHU's Power | kW | 1 Minute | 1 |  |  | 1 | 1 | Minimise Total AHUs Specific Power | Total AHU's Specific Power (kW)
Building | Sum AHU's Energy | kWh | 1 Minute | 1 |  |  | 1 | 1 | Maximise Ventilation Efficiency | Ventilation Efficiency (%)
[9 empty] | Monitor OA Temp Fraction | Outside air temperature fraction (Decimal)
[9 empty] | Monitor OA Damper Fraction | OA Damper Fraction
[9 empty] | Monitor OA Enthalpy Fraction | Outside Air Enthalpy Fraction
Water Services
Building | Total Water Services Electricity | kWh | 1 Minute | [8 empty] | Total Water Services electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Plug Loads
Building | Total Plug Loads Elec Meter | kWh | 1 Minute | 1 |  |  | 1 | 1 | Plug Load Electricity Use | Electricity Use (kWh) |  | Total plug loads electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
[9 empty] | Minimise Equipment Peak Load | Equipment Peak Load (kWh)
[9 empty] | Minimise Equipment EUI | Plug Loads EUI (kWh/M2)
People Movers
Building | Total People Movers Elec meter | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise People Mover Elec | People Mover Energy Use (kWh) |  | Total people movers electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Compressed Air
| Total Compressed Air Elec Meter | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | Total compressed electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Renewables
Building | Total Renewables Elec Meter | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | This measurement enables an overview of renewable system performance. It is a cumulative reading for solar thermal, photovoltaic and wind generated electricity respectively. These measurements enable a rapid evaluation of renewable technology performance. Without these measurements post operational evaluation is not achievable for these components.
Building | Total Renewables Heat Meter | kWh | 1 Minute
Building Tennant | Tennant Elec Sub Meter (kWh) | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise Storey Elec Consumption | Storey Electrical Consumption (kWh) |  | A building story electrical meter is included in the generic set of measurements to account for building tenants that may occupy an individual floor. It is unrealistic to apportion building energy consumption any other way.
Building Tennant | Tennant Gas Sub Meter (m3) | m3 | 1 Minute | 1 |  |  | 1 | 1
Building Tennant | Tennant Gas Sub Meter (m3) | m3 | 1 Minute | 1 |  |  | 1 | 1
Zone | Zone Temp | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Maintain Zone Temp | Zone Temperature (oC) |  | In normal office environments temperature is the key variable required. Zones containing art work or swimming pools may require tight humidity control. If zones are occupied then an energy manager requires the appropriate data stream that reflects this. Where possible zones should not be conditioned unless occupied or have strict indoor environmental requirements. An occupancy level can be used for comparison with zone plug loads and zone lighting levels and also helps establish micro-zones. A door/window closed signal would enable automatic shut off of air conditioning systems if a door or window was open. This measurement should be included for each aperature. Metabolic rate and air velocity are required for naturally ventilated spaces. Mean radiant temperature is required for zones with under floor heating of chilled beams. Zone lux levels are required where day lighting strategies are incorporated.
Zone | Zone Temp Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Maintain Zone Temp | Zone Temperature (oC)
Zone | Zone Relative Humidity | % | 1 Minute | 1 |  | 1 | 1 | 1 | Maintain zone RH | Zone RH
Zone | Zone Relative Humidity Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Zone | Occupancy Signal (CO2or PIR) | CO2 PPM | 1 Minute | 1 |  |  | 1 | 1 | Maintain Zone Humidity | Zone Humidity (%)
Zone | Zone Air Velocity | m/s | 1 Minute | 1 |  |  | 1 | 1 | Monitor Air Velocity | Zone Air Velocity (m/s) |  |  | Especially for naturally ventilated spaces
Zone | Zone Mean Radiant Temp | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Maintain Thermal Comfort Critera | Predicted Mean Vote (PMV)
Zone | Metabolic Rate | w/m2 | 1 Minute | 1 |  |  |  | 1 |  |  |  | From a Table
Zone | Doors/Windows Closed (Yes/No) | Yes/No | 1 Minute | 1 |  |  | 1 | 1 | Monitor Zone Integrity | Zone Integrity Signal (Windows and Doors Closed??) |  | For Each Door/Window
Zone | Magnitude of opening for each door or window | % | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | Only where natural ventilation is used.
Zone | Zone Lux Level | Lux | 1 Minute | 1 |  |  | 1 | 1 | Maintin Required Working Lux Levels | Zone Lux Levels
Zone | Zone Occupancy | People | 1 Minute | 1 |  |  |  | 1 | Monitor Zone Occupancy | Zone Occumpancy Level (No of People)
Zone | Zone Lighting load | kWh | 1 Minute | 1 |  |  |  | 1
Zone | Zone Plug Load | kWh | 1 Minute | 1 |  |  |  | 1
SYSTEMS |  |  | 1 Minute | [5 empty] | Minimise Air Sys Energy Use | Sys Energy Consumption (kWh)
Air System | Total Air System Elec | kWh | 1 Minute | 1 |  |  | 1 | 1 | Minimise AHU Total Power | Air Handler Total Power (Supply and Return) |  | The system supply air temperature, flow rate and serviced zone temperatures are key indicators of system performance. If the supply temperature and zone conditions are not satisfying their setpoint, then the system is not performing. These are critical measurements.
Air System | Supply Fan Elec (kWh) | kWh | 1 Minute | 1 |  |  |  | 1 |  |  |  | Duct static pressure may be used when diagnosing problems with maintaining Setpoints.
Air System | System On/Off Signal |  | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to.
Air System | System On/Off Status |  | 1 Minute | 1 |  |  | 1 | 1 | Minimise AHU Specific Power | AHU Specific Power (kW/M3)
Air System | Return Fan Elec | kWh | 1 Minute | 1 |  |  |  | 1 | Minimise Air Sys EUI | Sys EUI (kWh/M2) |  | Other measurements are duplicated by the components
Air System | Each Component Elec(kWh)/Area | kW | 1 Minute | 1 |  |  |  | 1 | Minimise Daily AHU Elec | Daily Total AHU Electrical Usage (kWh)
Air System | AHU Flow rate | m3 | 1 Minute | 1 |  |  | 1 | 1 | Minimise Daily Total AHU Volume | Daily Total AHU Volume (M3)
Air System | Zones Temps | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimise Peak AHU Volume | Daily Maximum AHU Volume (M3) |  |  | Duplicate measurement.Included for each zone object
Air System | MixA Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimise Daily Average AHU Power | Daily average Total AHU System Specific Power (kWh)
Air System | OA Temp | oC | 1 Minute | [5 empty] | Compare Air Flow and Outdoor DB | Daily Average Outdoor DB V Total Air Flow |  |  | Duplicate measurement refer to site
Air System | Return Air Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Monitor OA Temp Fraction | Outside air temperature fraction (Decimal)
Air System | Supply Air Temperature | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Monitor OA Damper Fraction | OA Damper Fraction
Air System | Duct Static Pressure | Pa | 1 Minute | 1 |  |  | 1 | 1
Air System | OA Air Damper Position | % | 1 Minute | 1 |  |  | 1 | 1
Air System | OA Damper Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Air System | Return Air Damper Position | % | 1 Minute | 1 |  |  | 1 | 1
Air System | Return Air Damper Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Air System | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Air System | Supply RH Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Air System | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Air System | Mix Air RH | % | 1 Minute | 1 |  |  | 1 | 1
Air System | Outside Air RH | % | 1 Minute | 1 |  |  | 1 | 1
Air System | Return Air RH | % | 1 Minute | 1 |  |  |  | 1
Air System | Supply Air Relative Humidity | % | 1 Minute | 1 |  | 1 | 1 | 1
Natural Ventilation System | Wind Speed | m/s | 1 Minute | [8 empty] | The critical measurement for this system type is the zone temperature. This measurement over a 24 hour period could influence system start up (opening times) and night ventilation strategies. | Duplicate measurement refer to site
Natural Ventilation System | Wind Direction | Degrees | 1 Minute | [8 empty] | For evaluation of a natural ventilation system, air velocity in the zone and at apertures must be recorded. Pressure at the windward and leeward façade would aid diagnostics. Aperture opening percentage is also required for system evaluation. | Duplicate measurement refer to site
Natural Ventilation System | Zone Temperature | oC | 1 Minute | [9 empty] | Duplicated Measurement refer to zone
Natural Ventilation System | Window Percentage Open | % | 1 Minute | [9 empty] | Duplicate measurement.Included for each zone object
Natural Ventilation System | Zones Temps | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimise Peak AHU Volume | Daily Maximum AHU Volume (M3) |  |  | Duplicate measurement.Included for each zone object
Natural Ventilation System | Zone Temp Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Maintain Zone Temp | Zone Temperature (oC) |  |  | Duplicate measurement.Included for each zone object
Natural Ventilation System | Natural Ventiation Power | kWh | 1 Minute | 1 |  |  |  | 1 | Minimise Natural Ventilation power Consumption | Natural Ventilation Power Consumption |  | Included to determine the net benefit of natural ventilation systems
Natural Ventilation System | Pressusre at Windward Façade | Pa | 1 Minute | 1 |  |  |  | 1
Natural Ventilation System | Pressusre at Leeward Façade | Pa | 1 Minute | 1 |  |  |  | 1
Fan | Fan Elec meter | kWh | 1 Minute | 1 |  |  |  | 1 | Minimise Fan Energy Consumption | Fan Energy Consumption (kWh) |  | The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to. Without these measurement streams each fan could operate when not required or consume excessive energy during normal operation. Duct static pressure may be required as a monitor of performance. Electricity meter would be a supplemental measurement and would be the lowest level of electrical consumption.
Fan | Air Flow Rate | m3 | 1 Minute | [5 empty] | Minimise VFD Speed Signal | VFD Fan Signal (Hz) |  |  | Duplicate measurement refer to air system
Fan | Fan VFD Signal Meter | % | 1 Minute | 1 |  |  | 1 | 1 | Maximise Fan Efficiency | Fan Efficiency (%)
Fan | Duct Total Pressure | Pa | 1 Minute | 1 |  |  | 1 | 1 | Monitor Fan Hours of Use | Hours Run (Must Find Out)
Fan | Fan Inlet Pressure | Pa | 1 Minute | 1 |  |  |  | 1
Fan | Fan Outlet Pressure | Pa | 1 Minute | 1 |  |  |  | 1
Fan | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Fan | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Fan Coil Unit | Supply in temp | oC | 1 Minute | 1 |  |  |  | 1 | Minimise Heating Energy use | Heating Energy Use (kWh) |  | The supply temperature is the critical measurement for this component. The effectiveness of the component can be monitored if zone temperature is compared with supply temperature. Unit operation can be determined by comparing outside air temperature and supply temperature. The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to. Component diagnostics could be performed using additional streams (air flow rate, water flow rate, water inlet and outlet temperatures). If heating is added by an electrical element this should be included as a separate meter.
Fan Coil Unit | Supply out temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Heating Efficiency | Heating Efficiency (%)
Fan Coil Unit | Supply Air flow rate | m3 | 1 Minute | 1 |  |  |  | 1 | Minimise Cooling Energy Use | Cooling Energy Use (kWh) |  | An electricity meter would be a supplemental measurement and would be the lowest level of electrical consumption.
Fan Coil Unit | If water based heating cooling same measurements for water side | % | 1 Minute | 1 |  |  |  | 1 | Maximise Cooling Efficiency | Cooling Efficiency (%)
Fan Coil Unit | Fan Elec | kWh | 1 Minute | 1 |  |  |  | 1
Fan Coil Unit | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Fan Coil Unit | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Fan Coil Unit | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Fan Coil Unit | Operational Status Signal | % | 1 Minute | 1 |  |  | 1 | 1
Mixing Box | Mixed Air Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maintain Setpoint | Mixing Box Setpoint (TempoC,(%) Humidity, Enthalpy kJ/kg) |  | The key measurement stream for this component is outlet temperature (compared with setpoint). If enthalpy control is used then the relative humidity and temperature are required for the outside air, return air and supply air streams. These measurement streams allow diagnosis of the mixing box component which if not operated properly can result in excessive energy consumption. Further diagnostics require the return and fresh air damper operational status and control signals are required. The supply air flow rate is also necessary. Without these measurements it is impossible to quantify and evaluate performance.
Mixing Box | Return Air Temp | oC | 1 Minute | 1 |  |  |  | 1 | Monitor Mixing Box Damper Position | Mixing Box Damper Position (%)
Mixing Box | Mixed Air relative humidty | % | 1 Minute | 1 |  |  | 1 | 1
Mixing Box | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Mixing Box | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Mixing Box | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Mixing Box | Supply Humidity Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Mixing Box | Return Air Relative Humidity (%) | % | 1 Minute | 1 |  |  |  | 1
Mixing Box | Damper Position Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Mixing Box | Damper position sensor | % | 1 Minute | 1 |  |  | 1 | 1
Mixing Box | Outside Air Temp | oC | 1 Minute | 1 |  |  |  | 1
Mixing Box | Outside Air Relative Humididty | % | 1 Minute | 1 |  |  |  | 1 |  |  |  | If enthalpy control is used | Duplicate Measurement Refer to Site
Mixing Box | Outside Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Mixing Box | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Mixing Box | Supply Air Flow rate | (m3/s) | 1 Minute | 1 |  |  | 1 | 1
Air to Air Heat Recovery | Supply in temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Energy Transfer | Air To Air HR Energy Transfer Rate (kW) |  | The objective of this component is to maximize the heat recovered from the return air stream. Outside air and the temperature of the air leaving the component give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required.
Air to Air Heat Recovery | Supply out temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Efficiency | Air to Air HR Efficiency (%)
Air to Air Heat Recovery | Supply air flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Supply in Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Return in temp | oC | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Return out temp | oC | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Supply in Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Air to Air Heat Recovery | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Air to Air Heat Recovery | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Air to Air Heat Recovery | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Supply in temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Energy Transfer | Air To Air HR Energy Transfer Rate (kW) |  | The objective of this component is to maximize the heat recovered from the return air stream. Outside air and the temperature of the air leaving the component give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to.
Thermal Wheel | Supply out temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Efficiency | Air to Air HR Efficiency (%)
Thermal Wheel | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Thermal Wheel | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Thermal Wheel | Supply Humidity Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Thermal Wheel | Supply air flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1 |  |  |  | Thermal wheels are prone to leaks and performance evaluation of such units should be undertaken where possible.
Thermal Wheel | Supply in Humidity Ratio | kg/kg | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Supply Out Humidity Ratio | kg/kg | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Return in temp | oC | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Return out temp | oC | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Supply in Humidity Ratio | kg/kg | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Supply Out Humidity Ratio | kg/kg | 1 Minute | 1 |  |  |  | 1
Thermal Wheel | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Thermal Wheel | Operational Status Signal | % | 1 Minute | 1 |  |  | 1 | 1
Heat Pipe | Supply in temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Heat Pipe Efficiency(Sensible Only) | Heat Pipe Efficiency (%) |  | The objective of this component is to maximize the heat recovered from the return air stream. The inlet and outlet temperatures give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required.
Heat Pipe | Supply out temp | oC | 1 Minute | 1 |  |  | 1 | 1
Heat Pipe | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Heat Pipe | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Heat Pipe | Supply Humidity Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Heat Pipe | Supply air flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Supply in Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Return in temp | oC | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Return out temp | oC | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Supply in Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Heat Pipe | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Heat Pipe | Operational Status Signal | % | 1 Minute | 1 |  |  | 1 | 1
Humidifier | Supply in temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimmise Humidificaion Load | Humididfication Load (kg/hour) |  | The critical measurement required for a humidifier is the outlet air relative humidity and temperature. Performance evaluation of the humidifier requires quantity of steam of sprayed water released to the supply air, the humidity ratio, temperature of the supply air and the humidity ratio of the outlet air. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to.
Humidifier | Supply out temp | oC | 1 Minute | 1 |  |  | 1 | 1
Humidifier | Supply air flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Humidifier | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Humidifier | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Humidifier | Supply Humidity Setpoint | % | 1 Minute | 1 |  | 1 | 1 | 1
Humidifier | Supply in Relative Humidity | % | 1 Minute | 1 |  |  |  | 1
Humidifier | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  | 1 | 1
Humidifier | Make Up Water | l/hour | 1 Minute | 1 |  |  |  | 1
Humidifier | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Humidifier | Operational Status Signal | % | 1 Minute | 1 |  |  | 1 | 1
Dehumidifier | Supply in temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Performance Efficicency | Humidifier Efficicency (%) |  | See cooling coil but must be accompanied by a heating coil
Dehumidifier | Supply out temp | oC | 1 Minute | 1 |  |  |  | 1
Dehumidifier | Supply air flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Dehumidifier | Supply in Relative Humidity (%) | % | 1 Minute | 1 |  |  | 1 | 1
Dehumidifier | Supply Out Relative Humidity | % | 1 Minute | 1 |  |  | 1 | 1
Dehumidifier | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Dehumidifier | Operational Status Signal | % | 1 Minute | 1 |  |  | 1 | 1
Dehumidifier | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Dehumidifier | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Diffuser | Supply Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Control Supply Temperature | Supply Air Temperature (oC) |  | The supply temperature is the key measurement for a diffuser. In certain circumstances the relative humidity of the supply air is also required. Air velocity and duct static pressure may be required if supply temperature is not satisfactory or there are occupant complaints due to drafts. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to. | Duplicate Measurement refer to Air System
Diffuser | Supply Air Velocity |  | 1 Minute | 1 |  |  |  | 1 | Control Supply Air Velocity | Supply Air Velocity (M3)
Diffuser | Supply Air Flow Rate | (m3/s) | 1 Minute | 1 |  |  |  | 1 | Control Air Flow Rate | Supply Air Flow Rate (M/S)
Diffuser | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Diffuser | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Diffuser | Supply Duct Air Pressure |  | 1 Minute | 1 |  |  |  | 1 | Control Pressure | Duct Pressure (Pa)
Diffuser | Supply Air Humidity | % | 1 Minute | 1 |  |  |  | 1 | Contol Humidity | Supply Air Relative Humidity (%)
Diffuser | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Diffuser | Actuator Position | % | 1 Minute | 1 |  |  | 1 | 1
FumeHood | Fume Hood Elec Meter | kWh | 1 Minute | 1 |  |  |  | 1 | Mimimise Elec Consumption | Elec Use (kWh) |  | The critical measurement here is an indicator of if an experiment is in progress or not. Combined with the on/off status optimum operation can be achieved. The electrical meter on the fume hood would be required to quantify electrical energy consumption. It is not a critical measurement.
FumeHood | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
FumeHood | On/Off Status | % | 1 Minute | 1 |  |  | 1 | 1 | Monitor Hours of Use | Hours of Use (Hours)
FumeHood | Experiment In Progress | Yes/No | 1 Minute | 1 |  |  |  | 1
Dual Duct Box | Zone Temp | oC | 1 Minute | [5 empty] | Maintain Supply Temperature | Supply Air Temperature (oC) |  | The key measurement stream for this component is supply temperature (compared with setpoint). For component diagnostics the Hot and cold damper operational status and control signals are required. The supply air flow rate is also necessary. Without these measurements it is impossible to quantify and evaluate performance. | Duplicate Measurement Refer to Zone
Dual Duct Box | Supply Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Maintain Supply Air Flow Rate | Supply Volumetric Flow Rate (M3/S) |  |  | Duplicate Measurement Refer to Air System
Dual Duct Box | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Dual Duct Box | Hot Damper | % | 1 Minute | 1 |  |  |  | 1 | Maintain Supply Air Humdidty | Supply Air Humidity (%)
Dual Duct Box | Cold Damper | % | 1 Minute | 1 |  |  |  | 1
Dual Duct Box | Air Flow Rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Dual Duct Box | Control Signal hot Damper | % | 1 Minute | 1 |  |  |  | 1
Dual Duct Box | Control Signal Cold Damper (%) | % | 1 Minute | 1 |  |  |  | 1
Dual Duct Box | Supply Temp Setpoint | oC | 1 Minute | [9 empty] | Value but not a measurement
Heating Coil | [12 empty] | Duplicate Object contained in Air System
Cooling Coil | [12 empty] | Duplicate Object contained in Air System
Compressed Air | Elec In | kWh | 1 Minute | 1 |  |  | 1 | 1 | Maximise Effectiveness | kWh per Nominal meters cubed(kWh/Nm3) |  | The important variables for evaluating the performance of a compressed air system are the Electricity in and the volume of air produced. The control signal and operational status are also required to ensure the compressed air system is operating as intended when it is supposed to.
Compressed Air | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Compressed Air | Nominal Air Volume Produced | m3 | 1 Minute | 1 |  |  | 1 | 1
Compressed Air | On/Off Status | % | 1 Minute | 1 |  |  | 1 | 1
Compressed Air | Operational Signal | % | 1 Minute | 1 |  |  | 1 | 1
Chilled Plant | Cooling Plant Elec |  | 1 Minute | 1 |  |  | 1 | 1 | Minimise Chiled Plant Power | Total Chillers Power |  | This level of measurement is required for large installations with more than one plant component used for cooling. The Electricity total is an aggregation of the individual components consumption. However this should be its own individual measurement to ensure consistency within the system as a whole. | These measurments may be applied to individual heating plant if required in a smaller building
Chilled Plant | Chilled Water Plant Supply out temp | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Minimise Chilled Plant Output | Total Chillers Output |  | The chilled plant cooling output (flow rate, inlet and outlet fluid temperatures) is also required to deliver an overall efficiency. For plant maintenance the condenser circuit also requires monitoring. Flow rate, inlet and outlet fluid temperatures are required to determine the heat rejected by the overall chilled plant system.
Chilled Plant | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Plant | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Plant | Chilled Water Plant Supply in temp | oC | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Plant | Demand Flow Rate | (m3/s) | 1 Minute | 1 |  | 1 | 1 | 1 | Monitor Chilled Plant Heat of Rejection | Total Chilled Water Plant Heat of Rejection (kWh)
Chilled Plant | Sum Condenser Loops Load | kWh | 1 Minute | 1 |  |  | 1 | 1 | Monitor Chill Water Plant Heat Balance | Chilled Water Plant Heat Balance (kWh)
Chilled Plant | Condenser Loops out temp | oC | 1 Minute | 1 |  |  | 1 | 1
Chilled Plant | Condenser Loops in temp | oC | 1 Minute | 1 |  |  | 1 | 1
Chilled Plant | Condenser Loops Flow Rate | (m3/s) | 1 Minute | 1 |  |  | 1 | 1
Secondary Chilled Water Loop | Primary Circuit Water Inlet Temp | oC | 1 Minute | [9 empty] | Duplicate Measurement refer to Chilled Plant
Secondary Chilled Water Loop | Mains Water Temperature | oC | 1 Minute | [9 empty] | Duplicate Measurement refer to Utility 'Water'
Secondary Chilled Water Loop | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Secondary Chilled Water Loop | Secondary Circuit Water Flow Temp | oC | 1 Minute | 1 |  | 1 | 1 | 1
Secondary Chilled Water Loop | Secondary Circuit Return Water Temp | oC | 1 Minute | 1 |  | 1 | 1 | 1
Secondary Chilled Water Loop | Secondary Circuit Water Flow rate | (m3/s) | 1 Minute | 1 |  | 1 | 1 | 1
Secondary Chilled Water Loop | Primary Circuit Water Flow Rate | (m3/s) | 1 Minute | 1 |  |  | 1 | 1
Secondary Chilled Water Loop | Valve Open | % | 1 Minute | 1 |  |  | 1 | 1
Secondary Chilled Water Loop | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Chiller | Elec Meter | kWh | 1 Minute | 1 |  |  |  | 1 | Minimise Chiller Energy Use | Chiller Energy Use (kW) |  | The electricity consumed and cooling delivered (flow rate, inlet and outlet water temperatures) are essential measurements for this component. A coefficient of performance can be determined from these values.
Chiller | Water Inlet Temp | oC | 1 Minute | 1 |  |  |  | 1 | Maximise Chiller COP | COP (Decimal Value) |  | The flow temperature alone is also a key indicator of how the chiller is conforming to design intent. The control signal and operational status are also required to ensure the boiler is operating as intended when it is supposed to.
Chiller | Water Outlet Temp | oC | 1 Minute | 1 |  |  |  | 1 | Monitor Chiller Load V Outdoor DB | Daily Average Outdoor DB V Daily Chiller Load |  | For plant maintenance the condenser circuit also requires monitoring. Flow rate, inlet and outlet fluid temperatures are required to determine the heat rejected by the condenser loop.
Chiller | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Chiller | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Chiller | Water Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1 | Monitor Chiller Hours of Use | Hours of Use (Hours)
Chiller | On/Off Status | % | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | Hours run meter is required for standard maintenance.
Chiller | Operational Signal | % | 1 Minute | 1 |  |  | 1 | 1
Chiller | Hours Run Meter |  | 1 Minute | 1 |  |  | 1 | 1
Cooling Tower | Refrigerant Supply Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Maximise Cooling Tower Heat Rejected | Cooling Tower Heat Loss (kWh) |  | The cooling tower heat rejected is of primary importance (Refrigerant Supply, ret temp, Condenser Circuit Flow Rate). These measurements when combined with cooling load delivered should illustrate chiller operation. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to. Outside air temperature is also an important indicator of heat rejection potential. Water cooled cooling towers also require wet bulb temperature of the air and volume of water used. Efficiency can be calculated using these measurement streams.
Cooling Tower | Refrigerant Return Temp | oC | 1 Minute | 1 |  | 1 |  | 1
Cooling Tower | Condenser Circuit Flow Rate | m3 | 1 Minute | 1 |  | 1 |  | 1 |  |  |  | The hours run meter is required for standard maintenance.
Cooling Tower | Make Up Water Flow Rate (If water Cooled) |  | 1 Minute | 1 |  |  |  | 1 |  | 3501
Cooling Tower | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Cooling Tower | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Cooling Tower | Operational Signal | % | 1 Minute | 1 |  |  | 1 | 1
Cooling Tower | Control Status | % | 1 Minute | 1 |  |  | 1 | 1
Cooling Tower | Hours Run Meter | Hours | 1 Minute | 1 |  |  | 1 | 1
Humidifier | [12 empty] | Duplicate Object contained in Air System
Condenser | Refrigerant Supply temp | oC | 1 Minute | 1 |  |  |  | 1 | Monitor Condenser Loop Load | Plant Condenser Loop Thermal Load (kWh) |  | The condenser loop load is of primary importance (Refrigerant Supply, ret temp, Condenser Circuit Flow Rate). These measurements when combined with cooling load delivered should illustrate chiller operation. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to. Outside air temperature and make up water used are also an important indicator of heat rejection potential. Water cooled condensers also require wet bulb temperature of the air. Efficiency can be calculated using this measurement stream.
Condenser | Refrigerant return temp | oC | 1 Minute | 1 |  |  |  | 1
Condenser | Condenser Circuit Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1
Condenser | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Condenser | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Condenser | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Condenser | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Condenser | Hours Run Meter |  | 1 Minute
Pump | [8 empty] | Refer to 6201 |  |  |  | Duplicate Object Contained in Hot Water Systems
Cooling Coil | Air Inlet Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimise Required Energy Transfer Rate | Cooling Coil Energy Use (kWh) |  | The Valve operational status and control signal are critical measurements for a heating coil. The air side outlet temperature can be compared with a setpoint to determine coil effectiveness. If the operational status and control signal measurements are absent then ineffective coil operation cannot be identified.
Cooling Coil | Air Outlet Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Efficiency | Cooling Coil Efficiency (%) |  | For component diagnosis the flow rate, inlet and outlet temperatures are required for both the air and water side. Fouling can be identified by quantifying efficiency over an extended time period.
Cooling Coil | Air Flow Rate |  | 1 Minute | 1 |  |  |  | 1
Cooling Coil | Water Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1
Cooling Coil | Water Outlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1
Cooling Coil | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Cooling Coil | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Cooling Coil | Water Flow Rate | m3 | 1 Minute | 1 |  | 1 |  | 1
Cooling Coil | Coil Valve | % | 1 Minute | 1 |  |  | 1 | 1
Cooling Coil | Coil Valve Signal | % | 1 Minute | 1 |  |  | 1 | 1
Thermal Storage | Supply temp (oC) IN | oC | 1 Minute | 1 |  |  |  | 1 | Monitor Cold Storage Transfer In | Cold Storage Energy Transfer (kWh) |  | Cooling output (flow rate, inlet and outlet fluid temperatures) is the key measurement required for a thermal storage system. Efficiency of the system and thermal losses are determinable using these datum streams. The control signal and operational status are also required to ensure the thermal storage unit is operating as intended when it is supposed to. The supply temperature out is a direct measure of the storage temperature.
Thermal Storage | Flow rate (Water) IN (m3/s) | (m3/s) | 1 Minute | 1 |  |  |  | 1 | Monitor Cold Storage Use (OUt) | Cold Storage Energy use (kWh)
Thermal Storage | Supply temp (oC) Out | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Maximise Cold Storage Efficiency | Cold Storage Efficiency (%)
Thermal Storage | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Thermal Storage | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Thermal Storage | Flow rate (Water) Out (m3/s) | (m3/s) | 1 Minute | 1 |  |  | 1 | 1
Thermal Storage | Operational Signal (%) | % | 1 Minute | 1 |  |  | 1 | 1
Thermal Storage | Control Status (%) | % | 1 Minute | 1 |  |  | 1 | 1
Chilled Beam | Mean Radiant Temp(oC) | oC | 1 Minute |  |  |  | 1 |  | Minimise Energy Consumption | Energy Consumption (kWh) |  | Flow rate, inlet and outlet temperatures can be combined to deliver a cooling output of the chilled beam circuit. This cooling output can help establish the distribution of cooling within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of cooling used. The mean radiant temperature of the space is key objective when using this type of system. | Duplicate Measurement contianted in Zone Object
Chilled Beam | Inlet Temp (oC) | oC | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Beam | Outlet Temp (oC) | oC | 1 Minute | 1 |  | 1 |  | 1
Chilled Beam | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Beam | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Chilled Beam | Water Flow rate (m3/s) | (m3/s) | 1 Minute | 1 |  | 1 |  | 1
Chilled Beam | Valve Open (%) | % | 1 Minute | 1 |  |  | 1 | 1
Chilled Beam | Valve Signal (%) | % | 1 Minute | 1 |  |  | 1 | 1
Direct Evap Cool | Supply Inlet DB Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Saturation Effectiveness | Saturation Effectiveness (%) |  | The key variables are water flow rate (cost) and supply outlet dry bulb temperature. These variables indicate system performance. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to.
Direct Evap Cool | Supply Outlet DB Temperature | oC | 1 Minute | 1 |  |  | 1 | 1
Direct Evap Cool | Return(In WB) | oC | 1 Minute | 1 |  |  |  | 1 |  |  |  | Measurements required for efficiency of the indirect cooling include supply inlet temperature. Return inlet wet bulb, supply and return air flow rates. Careful monitoring of efficiency can result in lower operating costs.
Direct Evap Cool | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Direct Evap Cool | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Direct Evap Cool | Supply Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Direct Evap Cool | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Direct Evap Cool | Water Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Direct Evap Cool | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Direct Evap Cool | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Indirect Evap Cool | Supply Inlet DB Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Saturation Effectiveness | Saturation Effectiveness (%) |  | The key variables are water flow rate (cost) and supply outlet dry bulb temperature. These variables indicate system performance. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to.
Indirect Evap Cool | Supply Outlet DB Temperature | oC | 1 Minute | 1 |  |  | 1 | 1
Indirect Evap Cool | Return(In WB) | oC | 1 Minute | 1 |  |  |  | 1
Indirect Evap Cool | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Indirect Evap Cool | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Indirect Evap Cool | Supply Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1 |  |  |  | Measurements required for efficiency of the indirect cooling include supply inlet temperature. Return inlet wet bulb, supply and return air flow rates. Careful monitoring of efficiency can result in lower operating costs.
Indirect Evap Cool | Return Air Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Indirect Evap Cool | Water Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Indirect Evap Cool | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Indirect Evap Cool | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Roof Spray System | Pump Elec | kWh | 1 Minute | 1 |  |  |  | 1 | Maximise System Efficiency | Roof Spray System Efficiency (%) |  | Night sky temperature (measured at the site level) gives an overview of cooling potential.
Roof Spray System | Make up Water Volume | m3 | 1 Minute | 1 |  |  |  | 1 | Minimise Energy Use | Pump Electricity Use (kWh) |  | The electrical consumption and the volume of water added to the system are key variables. These are energy and cost inputs. The outlet temperature from the roof, the outlet valve status and the outlet valve control signal are required to monitor operation. Adding the temperature of the return water and the water flow rate measurements illustrate how the cooling achieved by the night sky system.
Roof Spray System | Inlet Temp to roof | oC | 1 Minute | 1 |  |  |  | 1 | Mimimise Make Up Water | Volume of Make up Water
Roof Spray System | Outlet Temp from roof | oC | 1 Minute | 1 |  |  |  | 1
Roof Spray System | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Roof Spray System | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Roof Spray System | Water Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1
Roof Spray System | Valve Open | % | 1 Minute | 1 |  |  | 1 | 1
Roof Spray System | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Heating System | Heating Plant Gas Meters | m3 | 1 Minute | 1 |  | 1 | 1 | 1 | Minimise Heating System Output | Total Boilers Output |  | This level of measurement is required for large installations with more than one plant component used for heating. The gas consumed total is an aggregation of the individual components consumption. However this should be its own individual measurement to ensure consistency within the system as a whole. | These measurments may be applied to individual heating plant if required in a smaller building
Heating System | Heating Plant Flow rate | l/s | 1 Minute | 1 |  | 1 | 1 | 1 | Minimise Heating Fuel Consumption | Total Boilers Gas Flow |  | The heating plant heat output (flow rate, inlet and outlet water temperatures) is also required to deliver an overall efficiency.
Heating System | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Heating System | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Heating System | Heating Plant Supply Temp In | oC | 1 Minute | 1 |  | 1 | 1 | 1
Heating System | Heating Plant Supply Temp Out | oC | 1 Minute | 1 |  | 1 | 1 | 1
Secondary Hot Water Loop | [12 empty] | Duplicate Object Same as Secondary Chilled Water Loop
Boiler | Boiler Gas | m3 | 1 Minute | 1 |  |  | 1 | 1 | Maximise Boiler Efficiency | Boiler Efficiency (%), Boiler Runtime (Hours) |  | The boiler fuel consumed and heat output (flow rate, inlet and outlet water temperatures) are essential measurements for this component. The flow temperature alone is also a key indicator of how the boiler is conforming to design intent. The control signal and operational status are also required to ensure the boiler is operating as intended when it is supposed to.
Boiler | Inlet Temp | oC | 1 Minute | 1 |  |  |  | 1 | Minimise Boiiler Gas Flow | Total Boiler Gas Flow
Boiler | Outlet Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Monitor Boiler Gas V Outdoor DB | Daily Average Outdoor DB V Daily Boiler Load |  | Hours run meter is required for standard maintenance.
Boiler | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Boiler | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Boiler | Water Flow rate | (m3/s) | 1 Minute | 1 |  |  |  | 1 | Monitor Daily Gas Consumption | Maximum Daily Total Boiler Heating Energy
Boiler | On/Off Status | % | 1 Minute | 1 |  |  | 1 | 1 | Monitor Boiler Hours of Use | Hours of Use (Hours)
Boiler | Boiler Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Boiler | Hours Run Meter |  | 1 Minute | 1 |  |  | 1 | 1
Solar Photovoltaic | PV Elec Meter | kWh | 1 Minute | 1 |  | 1 | 1 | 1 | Maximise Total PV Production | Total PV System Production (kWh/Time Period) |  | Solar radiation and electricity produced are the key measurements for PV panels. The control signal is also an essential measurement as electricity is needed instantly if required.
Solar Photovoltaic | Solar Radiation | kWh | 1 Minute | 1 |  |  |  | 1 | Maximise Net PV Production | Net PV System Production (kWh/Time Period) |  | If these readings are absent. Excessive electricity may be purchased from the grid resulting in higher costs. Also peak power required from the grid may be increased with the potential for further higher tariffs. | Duplicate measurement refer to Site
Solar Photovoltaic | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Solar Photovoltaic |  |  | 1 Minute | [5 empty] | Maximise Equivalent Annual Hours | Equivalent Annual Hours Peak PV Product(hrs/yr/kWp)
Solar Photovoltaic |  | % | 1 Minute | [5 empty] | Maximise Offset Facility Elec Load | Facility Electrical Load Offset by PV Production (%)
Solar Photovoltaic |  | % | 1 Minute | [5 empty] | Maximise Offset Facility Total Load | Facility Total Energy Load Met by PV Production (%)
Solar Photovoltaic |  | kWh/Time | 1 Minute | [5 empty] | Monitor Total Elec Exported | Total Electricity Exported to Utility (kWh/Time)
Solar Photovoltaic |  | kWh | 1 Minute | [5 empty] | Monitor Total Incident Solar | Total Incident Solar Radiation (kWh)
Solar Photovoltaic |  | % | 1 Minute | [5 empty] | Maximise PV Effectiveness | PV System AC Electricity Generation Effectiveness (%)
Solar Photovoltaic |  | % | 1 Minute | [5 empty] | Maximise PV Performance Ratio | PV System Performance Ratio (%)
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Minimise Net Facility Energy Use | Net Facility Electricity Use (kWh/Time)
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Minimise Peak Elec Demand | Peak Demand of Net Facility Electricity Use(kW/Time )
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Mimimise Total Peak Demand | Peak Demand of Total Facility Elec Use without PV(kW)
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Maximise Peak Demand Reduction | Reduction of Peak Demand because of PV system (kW)
Solar Photovoltaic |  | Euro | 1 Minute | [5 empty] | Minimise Elec Costs | Facility Electricity Costs without PV System (Currency)
Solar Photovoltaic |  |  | 1 Minute | [5 empty] | Maximise PV Energy Cost Savings | Energy Cost Savings Resulting from PV System(Currency)
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Maximise Average PV Production | Maximum Time-Series Net PV Production (kW/Time)
Solar Photovoltaic |  | kW | 1 Minute | [5 empty] | Maximise Daily Average PV Product | Average Daily Time-Series PV Production (kW V time)
Solar Photovoltaic | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Solar Water Heater | Solar Radiation | kWh | 1 Minute | [5 empty] | Maximise Solar Water Heating | Solar Water Heating Delivered (kWh) |  | Solar radiation and heat delivered (flow rate, inlet and outlet water temperatures) to the hot water are key measurements here. Combined they deliver the effectiveness and efficiency of the system. The flow temperature is required on its own as if a system limits are exceeded catastrophic failure can occur. The control signal and operational status are also required to ensure the solar water heater is operating as intended when it is supposed to. | Duplicate Measurement refer to Site
Solar Water Heater | Water Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Maximise Solar Water Efficiency | Solar Water Heating Efficiency (%)
Solar Water Heater | Water Outlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Maximise Solar % of Total Heating | Percentage of Total Heating (%)
Solar Water Heater | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Solar Water Heater | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Solar Water Heater | Water Flow Rate | m3 | 1 Minute | 1 |  | 1 |  | 1 | Maximise Savings | Resultant Energy Savings (Unito of Local Currency)
Solar Water Heater | Valve Open | % | 1 Minute | 1 |  |  |  | 1
Solar Water Heater | Control Signal | % | 1 Minute | 1 |  |  |  | 1
Furnace | Furnace Gas Meter | (m3/s) | 1 Minute | 1 |  |  |  | 1 | Maximise Furnace Efficiency | Furnace Efficiency (%) |  | Fuel consumption and heat output (flow rate, inlet and outlet water temperatures) are critical measurements. Overall unit efficiency and energy consumption can be determined using these measurements. The control signal and operational status are also required to ensure the furnace is operating as intended when it is supposed to.
Furnace | Water Inlet Temp | oC | 1 Minute | 1 |  |  |  | 1 | Minimise Furnace Energy Use | Furnace Energy Output (kW)
Furnace | Water Outlet Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Minimise Furnace Gas Flow | Total Furnace Gas Flow |  | If any of these datum streams are absent then the unit has the potential to operate inefficiently.
Furnace | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Furnace | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Furnace | Water Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1 | Monitor Furnace Gas V Outdoor DB | Daily Average Outdoor DB V Daily Furnace Load |  | Hours run meter is required for standard maintenance.
Furnace | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1 | Monitor Daily Gas Consumption | Maximum Daily Total Furnace Heating Energy
Furnace | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Furnace | Hours Run Meter | Hours | 1 Minute
CHP | Fuel Meter | (m3/s) | 1 Minute | 1 |  |  | 1 | 1 | Maximise CHP Efficiency | CHP Total Efficiency (%) |  | Fuel consumption, heat output (flow rate, inlet and outlet temperatures) and electricity produced are critical measurements. Overall unit efficiency and energy consumption can be determined using these measurements. The control signal and operational status are also required to ensure the CHP unit is operating as intended when it is supposed to.
CHP | Elec Output | kWh | 1 Minute | 1 |  |  | 1 | 1 | Monitor Elec Production | CHP Elec Production (kWh)
CHP | Water Flow Rate | (m3/s) | 1 Minute | 1 |  |  | 1 | 1 | Monitor Elec Production Efficiency | CHP Elec Efficiency (%) |  | If any of these datum streams are absent then the unit has the potential to operate inefficiently.
CHP | Water Inlet Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Monitor Heat Production | CHP Heat Production (kWh) |  | Hours run meter is required for standard maintenance.
CHP | Water Outlet Temp | oC | 1 Minute | 1 |  |  | 1 | 1 | Monitor Heat Production Efficiency | CHP Heat Efficiency (%)
CHP | Electriciyt Output Setpoint | kWh | 1 Minute | 1 |  |  | 1 | 1
CHP | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
CHP | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
CHP | Hours Run Meter | Hours | 1 Minute | 1 |  |  | 1 | 1
CHP | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
CHP | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Heat Pump | Elec Meter | kWh | 1 Minute | 1 |  |  |  | 1 | Opearation History | Time (%) |  | Electricity input is a key measurement for a building manager. The control signal and operational status are also required to ensure the heat pump is operating as intended when it is supposed to.
Heat Pump | Supply side Water Inlet Temp | oC | 1 Minute | 1 |  |  |  | 1 | Maximise COP | COP (Decimal Value)
Heat Pump | Supply Side Water Outlet Temp | oC | 1 Minute | 1 |  |  |  | 1 |  |  |  | Fluid flow rate, inlet and outlet temperatures for the supply and demand sides are required to determine the coefficient of performance for a heat pump. Without these measurements it is impossible to determine if the heat pump is operating as it was intended to.
Heat Pump | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Heat Pump | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Heat Pump | Supply Side Water Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1
Heat Pump | Demand side Water Inlet Temp( | oC | 1 Minute | 1 |  |  |  | 1 |  |  |  | Hours run meter is required for standard maintenance.
Heat Pump | Demand Side Water Outlet Temp | oC | 1 Minute | 1 |  |  | 1 | 1
Heat Pump | Demand Side Water Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1
Heat Pump | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Heat Pump | Operational Status | % | 1 Minute | 1 |  |  | 1 | 1
Heat Pump | Hours Run Meter | Hours | 1 Minute | 1 |  |  | 1 | 1
DHW | Water Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Minimise DHW Use | DHW Load (KWh) |  | The critical measurements for this circuit are flow temperature (to avoid burning), return temperature and flow rate. Combined these measurements also deliver the heat delivered to the domestic hot water circuit. This reading is required to understand the end use of heat in the building.
DHW | Water Outlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1
DHW | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
DHW | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
DHW | Water Flow Rate | m3 | 1 Minute | 1 |  | 1 |  | 1 |  |  |  | If the flow rate is absent leaks or dripping taps may go unnoticed.
DHW | DHW Valve | % | 1 Minute | 1 |  |  | 1 | 1
DHW | Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Heating Coil | Air Inlet Temperature | oC | 1 Minute | 1 |  |  |  | 1 | Minimise Required Energy Transfer Rate | Heating Coil Energy Use (kW) |  | The Valve operational status and control signal are critical measurements for a heating coil. The air side outlet temperature can be compared with a setpoint to determine coil effectiveness. If the operational status an control signal measurements are absent then ineffective coil operation cannot be identified.
Heating Coil | Air Outlet Temperature | oC | 1 Minute | 1 |  |  | 1 | 1 | Maximise Efficiency | Heating Coil Efficiency (%) |  | For component diagnosis the flow rate, inlet and outlet temperatures are required for both the air and water side. Fouling can be identified by quantifying efficiency over an extended time period.
Heating Coil | Air Flow Rate | m3 | 1 Minute | 1 |  |  |  | 1
Heating Coil | Water Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1
Heating Coil | Water Outlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1
Heating Coil | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Heating Coil | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Heating Coil | Water Flow Rate | m3 | 1 Minute | 1 |  | 1 |  | 1
Heating Coil | Coil Valve | % | 1 Minute | 1 |  |  | 1 | 1
Heating Coil | Coil Valve Signal | % | 1 Minute | 1 |  |  | 1 | 1
Pump | Flow meter | l/s | 1 Minute | 1 |  |  |  | 1 | Maximise Efficiency | Pump Efficiency (%) |  | Electrical meter for all pumps. The flow meter, inlet and outlet pressures, operational status and control signal are all required for advanced diagnostics. These are more useful for pumps with a variable speed drive.
Pump | Elec meter | kWh | 1 Minute | 1 |  |  |  | 1 | Minimise Energy Use | Pump Energy Use (kWh)
Pump | Inlet Total Pressure | Pa | 1 Minute | 1 |  |  |  | 1 | Monitor Pump Hours of Use | Hours of Use (Hours)
Pump | Outlet Total Pressure | Pa | 1 Minute | 1 |  |  |  | 1
Pump | Pressure Setpoint | Pa | 1 Minute | 1 |  |  | 1 | 1
Pump | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Pump | On/Off Status | % | 1 Minute | 1 |  |  | 1 | 1
Pump | Pump Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
Water Storage | Tank Water Temperature (oC) | oC | 1 Minute | 1 |  | 1 | 1 | 1 | Monitor Water Temp | Water Temp (Degrees C) |  | Maintaining the tank water temperature is the key objective here. It is a critical measurement.
Water Storage | Supply Circuit Inlet Temp | oC | 1 Minute | [8 empty] | Advanced diagnostics require quantification of heat in and heat out of the water tank. Flow rate, Inlet and outlet temperature are required for both the demand and supply circuits. Without these measurements it is impossible to determine heat losses from the tank.
Water Storage | Storage Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Water Storage | Supply Circuit Outlet Temp | oC | 1 Minute
Water Storage | Supply Circuit Flow rate | (m3/s) | 1 Minute
Water Storage | Demand+D2 Circuit Inlet Temp | oC | 1 Minute
Water Storage | UFH Circuit Outlet Temp | oC | 1 Minute
Water Storage | UFH Circuit Flow rate | (m3/s) | 1 Minute
Under Floor Heating | UFH Circuit Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Minimise Energy Consumption | Energy Consumption (kWh) |  | Flow rate, inlet and outlet temperatures can be combined to deliver a heat output of the under floor heating circuit. This heat output can help establish the distribution of heat within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of heat used. The mean radiant temperature of the space is key objective when using this type of system.
Under Floor Heating | UFH Circuit Outlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 |  |  |  | If these reading are combined with valve position and control signal then diagnostics can be performed on the circuit.
Under Floor Heating | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Under Floor Heating | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Under Floor Heating | UFH Circuit Flow rate | (m3/s) | 1 Minute | 1 |  | 1 |  | 1
Under Floor Heating | Mean Radiant Temperature | oC | 1 Minute | 1 |  |  | 1 | 1
Under Floor Heating | UFH Circuit Valve Position | % | 1 Minute | 1 |  |  | 1 | 1
Under Floor Heating | UFH Circuit Valve Position | % | 1 Minute | 1 |  |  | 1 | 1
Radiator Circuit | Radiator Circuit Inlet Temp | oC | 1 Minute | 1 |  | 1 |  | 1 | Minimise Energy Consumption | Energy Consumption (kWh) |  | Flow rate, inlet and outlet temperatures can be combined to deliver a heat output of the radiator circuit. This heat output can help establish the distribution of heat within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of heat used.
Radiator Circuit | Radiator Circuit Oulet Temp | oC | 1 Minute | 1 |  | 1 | 1 | 1 |  |  |  | If these reading are combined with valve position and control signal then diagnostics can be performed on the circuit.
Radiator Circuit | Supply Temperature Setpoint | oC | 1 Minute | 1 |  | 1 | 1 | 1
Radiator Circuit | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Radiator Circuit | Raiator Flow rate | (m3/s) | 1 Minute | 1 |  | 1 |  | 1
Radiator Circuit | Radiator Circuit Valve Position | % | 1 Minute | 1 |  |  | 1 | 1
Radiator Circuit | Radiator Circuit Control Signal | % | 1 Minute | 1 |  |  | 1 | 1
People Mover Sys | Total People Movers Elec Meter | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | This measurement on its own can identify where electricity is being used in a building, if it is a constant load throughout out the day or not and if people mover systems are running during unoccupied hours.
Elevator | Occupancy (CO2) | PPM | 1 Minute | 1 |  |  |  | 1 | Minimise Elevator Electricity | Energy Use (kWh) |  | These measurement streams can determine the operation of an individual elevator system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
Elevator | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Elevator | Elevator Elect | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
Elevator | Control Signal | % | 1 Minute | 1 |  |  |  | 1
Elevator | Operational Status | % | 1 Minute | 1 |  |  |  | 1
Escalator | Occupancy (CO2) | PPM | 1 Minute | 1 |  |  |  | 1 | Minimise Escalator Electricity | Energy Use (kWh) |  | These measurement streams can determine the operation of an individual escalator system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
Escalator | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Escalator | Escalator Elec | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
Escalator | Control Signal | % | 1 Minute | 1 |  |  |  | 1
Escalator | Operational Status | % | 1 Minute | 1 |  |  |  | 1
Walkway | Occupancy (CO2) | PPM | 1 Minute | 1 |  |  |  | 1 | Minimise Walkway Electricity | Energy Use (kWh) |  | These measurement streams can determine the operation of an individual walkway system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
Walkway | Operating Schedule | Time | 1 Minute | 1 |  | 1 | 1 | 1
Walkway | Walkway Elec | kWh | 1 Minute | 1 |  |  | 1 | 1 |  |  |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
Walkway | Control Signal | % | 1 Minute | 1 |  |  |  | 1
Walkway | Operational Status | % | 1 Minute | 1 |  |  |  | 1

## LEED_Credits
Code | Credit Descritpion | Relevant | Relevant Object | Comment
LEED Credit Group: Sustainable Sites
SS Prerequisite 1: Construction Activity Pollution Prevention
SS Credit 1: Site Selection
SS Credit 2: Development Density & Community Connectivity
SS Credit 3: Brownfield Redevelopment
SS Credit 4.1: Alternative Transportation: Public Transportation Access
SS Credit 4.2: Alternative Transportation: Bicycle Storage & Changing Rooms
SS Credit 4.3: Alternative Transportation: Low Emitting & Fuel Efficient Vehicles
SS Credit 4.4: Alternative Transportation: Parking Capacity
SS Credit 5.1: Site Development: Protect or Restore Habitat
SS Credit 5.2: Site Development: Maximize Open Space
SS Credit 6.1: Stormwater Design: Quantity Control
SS Credit 6.2: Stormwater Design: Quality Control
SS Credit 7.1: Heat Island Effect: Non-Roof
SS Credit 7.2: Heat Island Effect: Roof
SS Credit 8: Light Pollution Reduction
WEC1 | WE Credit 1.1: Water Efficient Landscaping: Reduce by 50%
WE Credit 1.2: Water Efficient Landscaping: No Potable Water Use or No Irrigation
WEC2 | WE Credit 2: Innovative Wastewater Technologies
WEC3 | WE Credit 3.1: Water Use Reduction: 20% Reduction | 1 | Utility Provider | This Credit Requires a Water Meter
| WE Credit 3.2: Water Use Reduction: 30% Reduction | 1 |  | This Credit Requires a Water Meter
LEED Credit Group: Energy & Atmosphere
EAP1 | EA Prerequisite 1: Fundamental Commissioning of the Building Energy Systems | 1 | Water and Air Systems | Commissioning of the Building Energy Systems}: This emphasis for this Credit is on a recorded and structured process. When applied to building systems the process requires Energy Management Tier 2 measurement streams for all HVAC systems and the zones which they service.
EAP2 | EA Prerequisite 2: Minimum Energy Performance | 1 | Building | Minimum Energy Performance}: This Credit requires compliance with the mandatory provisions and prescriptive requirements of ASHRAE/IESNA Standard 90.1-2004. In order to evaluate minimum energy performance fossil fuel use and electricity use need to be quantified at design. Building floor area is also required. The operational equivalent of this Credit is attainable through existing measurements.
EAP3 | EA Prerequisite 3: Fundamental Refrigerant Management
EAC1 | EA Credit 1: Optimize Energy Performance | 1 | Everything | The measurement streams defined by the Energy Management Rule Set are required for this credit but the datum source must be whole building simulation model output. The number of points allocated for this Credit (1-10 points) depends on a percentage reduction of projected energy consumption when compared with the standard prescriptive evaluation of the same building.
EAC2 | EA Credit 2: On-Site Renewable Energy | 1 | Renewables | This Credit requires measurement streams for the on-site renewable energy components.
EAC3 | EA Credit 3: Enhanced Commissioning | 1 | Everthing | This Credit requires the Energy Management View, Tier 3 measurement streams.
EAC4 | EA Credit 4: Enhanced Refrigerant Management
EAC5 | EA Credit 5: Measurement & Verification | 1 | Everything | This Credit requires the Energy Management View, Tier 2 measurement streams.
EAC6 | EA Credit 6: Green Power | 1 | Utility Provider | The utility provider data are required and present. The provider details, building electricity meter and tariff information are available.
LEED Credit Group: Materials & Resources
MR Prerequisite 1: Storage & Collection of Recyclables
MR Credit 1.1: Building Reuse: Maintain 75% of Existing Walls, Floors & Roof
MR Credit 1.2: Building Reuse - Maintain 95% of Existing Walls, Floors & Roof
MR Credit 1.3: Building Reuse: Maintain 50% of Interior Non-Structural Elements
MR Credit 2.1: Construction Waste Management: Divert 50% From Disposal
MR Credit 2.2: Construction Waste Management: Divert 75% From Disposal
MR Credit 3.1: Materials Reuse: 5%
MR Credit 3.2: Materials Reuse: 10%
MR Credit 4.1: Recycled Content: 10% (post-consumer + 1/2 pre-consumer)
MR Credit 4.2: Recycled Content: 20% (post-consumer + 1/2 pre-consumer)
MR Credit 5.1: Regional Materials: 10% Extracted, Processed & Manufactured Regionally
MR Credit 5.2: Regional Materials: 20% Extracted, Processed & Manufactured Regionally
MR Credit 6: Rapidly Renewable Materials
MR Credit 7: Certified Wood
LEED Credit Group: Indoor Environmental Quality
EQP1 | EQ Prerequisite 1: Minimum IAQ Performance | 1 | Zone | This Credit is used at the design stage. During operation the equivalent measurement streams are the volume of fresh air and number of occupants over time.
EQP2 | EQ Prerequisite 2: Environmental Tobacco Smoke (ETS) Control
EQC1 | EQ Credit 1: Outdoor Air Delivery Monitoring | 1 | HVAC System/Fan | This credit requires the installation of permanent monitoring systems that provide feedback on ventilation system performance to ensure that ventilation systems maintain design minimum ventilation requirements. Configure all monitoring equipment to generate an alarm when the conditions vary by 10\% or more from setpoint, via either a building automation system alarm to the building operator or via a visual or audible alert to the building occupants
EQC2 | EQ Credit 2: Increased Ventilation | 1 | HVAC System/Fan | This Credit utilises identical measurement streams as EQC1. However compliance with stricter air flow rate standards is required.
EQ Credit 3.1: Construction IAQ Management Plan: During Construction
EQ Credit 3.2: Construction IAQ Management Plan: Before Occupancy
EQ Credit 4.1: Low-Emitting Materials: Adhesives & Sealants
EQ Credit 4.2: Low-Emitting Materials: Paints & Coatings
EQ Credit 4.3: Low-Emitting Materials: Carpet Systems
EQ Credit 4.4: Low-Emitting Materials: Composite Wood & Agrifiber Products
EQ Credit 5: Indoor Chemical & Pollutant Source Control
EQC6 | EQ Credit 6.1: Controllability of Systems: Lighting | 1 | Zone | This Credit requires the Energy Management View, Tier 3 measurement streams at the zone level.
| EQ Credit 6.2: Controllability of Systems: Thermal Comfort | 1 | Zone | This Credit requires the Energy Management View, Tier 3 measurement streams at the zone level.
EQC7 | EQ Credit 7.1: Thermal Comfort: Design | 1 | Zone | This Credit requires the Energy Management View, Tier 3 zone measurement streams.
| EQ Credit 7.2: Thermal Comfort: Verification | 1 | Zone | This Credit requires the Energy Management View, Tier 3 zone measurement streams.
EQC8 | EQ Credit 8.1: Daylight & Views: Daylight 75% of Spaces | 1 | Zone | This Credit requires the Energy Management View, Tier 3 zone measurement streams.
| EQ Credit 8.2: Daylight & Views: Views for 90% of Spaces | 1 | Zone | This Credit requires the Energy Management View, Tier 3 zone measurement streams.
LEED Credit Group: Innovation & Design Process
ID Credit 1–1.4: Innovation in Design
ID Credit 2: LEED Accredited Professional
| Total Number of Relevant Credits | 18

## LEED_View
Performance Objects | Performance Objective | Performance Metric and Unit | WEC 3 | EAP 1 | EAP 2 | EAC 1 | EAC 2 | EAC 3 | EAC 5 | EAC 6 | EQ P1 | EQ C1 | EQC 2 | EQC 6 | EQC 7 | EQC 8 | Energy Manager | Measurements Required | Unit | Interval | Resolution | Description of Measurements | Comment
Site | Monitor Outdoor DB Temp | Outdoor Dry Bulb Temp (oC) |  | 1 |  | 1 | 1 | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | Outdoor DB Temp sensor | oC | 1 Minute |  | This measurement stream is the most important indicator of the nature of external conditions. This datum stream can be used to determine degree days and to understand the time lag between external temperatures and its effect on indoor environmental conditions. It can also and important measurement stream when optimizing economizer operation | North Façade in permanent shade
| Monitor Outdoor WB Temp | Outdoor Wet Bulb Temp (oC) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | South Façade Outdoor DB Temp sensor | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | East Façade Outdoor DB Temp sensor | oC | 1 Minute
| Moitor Outdoor % Humidity | Outdoor Humidity (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | West Façade Outdoor DB Temp sensor | oC | 1 Minute
| Monitor Average Daily DB Temp | Average Daily Outdoor Temp (oC) |  |  |  |  | 1 | [10 empty] | Outdoor WB Temp sensor | oC | 1 Minute |  | If this stream is missing, it is impossible to establish a link between external environmental conditions and zone conditions. | Either Wet Bulb or RH
| Monitor Heating Degree Days | Heating Degree Days (Dimensionless) |  | 1 |  | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | or OA Humididy | % | 1 Minute |  | This measurement stream can give an indication if supply air requires humidification. It can also be used for enthalpy based control of mixing boxes. If this stream is absent poor indoor environmental conditions may result.
| Monitor Cooling Degree Days | Heating Degree Days (Dimensionless)
| Monitor Wind Speed | Wind Speed (m/s) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Wind Velocity | m/s | 1 Minute |  | These measurement streams are vital in situations where natural ventilation is used. Independently high wind speeds can have a heating/cooling effect on a building. Extremely high wind speeds may also trigger an alarm to close all windows
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Wind Direction | Degrees | 1 Minute
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Solar Radiation | kWh | 1 Minute |  | This datum stream is used to determine the amount of solar radiation falling on a building. It is an essential measurement where PV and solar thermal systems are installed. Solar radiation can also be closely coupled with cooling electrical load.
If the solar radiation measurement stream is absent, then it is impossible to quantify the effect solar radiation has on building performance.
|  |  |  | 1 |  | 1 |  | 1 | 1 |  |  |  |  | 1 |  | 1 | 1 | Outdoor Natural Light Levels | Lux | 1 Minute |  | Outdoor natural light levels are a useful measurement where day-lighting strategies are in place. It quantifies available natural light that should act as a reference for natural light levels that are available indoors. This Lux measurement can also be used for the automated control of external lighting. If lighting is manually controlled it has the potential to consume more energy than is required.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Night Sky Radiant Temperature | oC | 1 Minute |  | This measurement is necessary for buildings that incorporate night sky cooling systems. It gives an indicator of the cooling potential on any particular night.
If this measurement is missing operational performance of the cooling system can not be determined.
Building |  |  |  | 1 |  | 1 |  | 1 | 1 |  | 1 | [5 empty] | 1 | Building Occupancy Level (Office Building) | People | 1 Minute |  | The purpose of this measurement is to define building function. This measurement (e.g. building occupancy level, units produced etc.) enables a comparison of organizational performance and energy consumption. Without this measurement stream it is difficult to make a fair comparison. If for example more people occupy a building in year 2 compare with year 1 it is highly probably that extra energy will be consumed in year 2 when compared with year 1.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Building Function (Units produced) | Units | 1 Minute
| Minimise Building Energy Use | Total Energy Use (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Occupant Satisfaction
| Minimise Builidng EUI | EUI (kWh/M2/Year) |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Floor Area (m2) | m2 | 1 Minute
| Minimise Builidng EUI | EUI (kWh/M3/Year) |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Building Volume (m3) | m3 | 1 Minute
| Minimise Total Energy Cost | Total Energy Cost (Unit of Local Currency)
| Normalized atmospheric emissions | Tons CO2
Primary Energy Use | Minimise HVAC Energy use | Total HVAC EUI (kWh/M2/Year) |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Bills (Monthly Monetary Values) | Euro | 1 Minute |  | Utility bills are used by financial controllers. Cost and energy consumption (kWh or m3) values are the key parameters. A calorific value is required to convert gas volumes of gas into kWh energy values. Without these measurement streams communication between the energy manager and financial controller is extremely difficult. | Duplicate refer to energy by utility
|  |  |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Energy Consumption | kWh/M2/Year | 1 Minute |  | The first level of understanding energy consumption can come from analyzing monthly energy consumption. E.g. is a higher electrical load in summer a result of additional cooling? 10 minute pricing information is critical where dynamic tariffs are used. If building area or building volume is used then an informative EUI can be established for a building.
| Minimise Electricity Use | Tolal Electrical Consumption (kWh) |  |  | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Energy Consumption, Volume | m3 | 1 Minute |  | Also an increase in Gas consumption would normally be expected in winter.
| Minimise peak power required | Whole Building Peak Power (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Bills (10 minute price information) | Euro | 1 Minute |  | If the resolution of measurement is reduced from monthly to a sub hourly time step a clearer picture of the operational characteristics of the building emerge. Start up times for the building can become clear. An energy manager can visualize the time at which peak electrical power occurs. A night time electrical baseline can be established. Initial understanding of gas consumption can be based on sub hourly readings. Again base lines and heating periods can be established (The same measurements and principles apply for oil and water use).
| Normalised Electricty Consumption | Electricty Consumption (kWh/Time Period) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Utiltiy bills (Monthly Consumption Values) | CO2 | 1 Minute
| Electrical EUI | Electrical EUI (kWh/M2/Year) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Elec & Gas Total/(Area Conditioned) | kWh/M2/Year | 1 Minute
| Electrical Cost | Electrical Cost (Unit of Local Currency)
| Minimise Electricity use | Average Daily Electrical Power (kWh)
Electricty | Minimise Gas Consumption | Total Gas Use (kWh) |  | 1 | 1 | 1 |  | 1 | 1 | 1 | [6 empty] | 1 | Electricity Bills (Cost) | Euro | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | 1 | [6 empty] | 1 | Electricity Energy Consumption | kWh | 1 Minute
| Minimise Gas Energy Use | Normalised Gas Consumption (kWh/Time Period) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Building Volume | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | 1 | [6 empty] | 1 | Electricity Bills (10 minute price information) | Euro | 1 Minute
| Minimise Oil Consumption | Total Oil USe (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Sum HVAC Elec Sub meters | kWh | 1 Minute
| Minimise Peak oil use | Building Peak Oil (kWh)
| Minimise oil Consumption | Normalised Oil Consumption (kWh/Time Period)
| Minimise Peak Water Consumption | Building Peak Water (M3)
Gas | Minimise water consumption | Normalised Water Consumption (M3) |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Gas Meter or Utilty Bill | m3 | 1 Minute
| Minimise water Use Intensity | Water UI (M3/M2) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Bills (Gas Cost) | Euro | 1 Minute
[18 empty] | Gas Calorific Value | kW | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Sum of HVAC Gas Meters | kWh | 1 Minute
| Minimise Peak Elec Cooling Load | Peak Elec Cooling Load (kW)
| Maximise Chilled Plant Efficiency | All Chillers Efficiency (%)
| Minimmise Cooling Load EUI | Minimise Cooling EUI (kWh/M2/Year)
| Minimmise Cooling Load EUI | Minimise Cooling EUI (kWh/M3/Year)
| Monitor Chilled Water Delta T | Chilled Water Loop Delta T (oC)
| Average Chilled Water Supply Temp | Average Daily Chilled water Supply Temp (oC)
Oil |  |  |  | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Oil Meter(M3) or Utilty Bill | m3 | 1 Minute
| Minimise Heating Load (Supply & Demand) | Heating Load (kWh & M3) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Utility Bills (Oil Cost) | kWh | 1 Minute
| Minimise Peak Heating Load | Peak Heating Load (kWh & M3) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Sum of HVAC Oil Meters | kWh | 1 Minute
| Maximise Heating Plant Efficiency | Boilers Efficiency (%)
| Minimise Heating Load EUI (Area) | Minimise Heating EUI (kWh/M2Area Heated/Year)
| Minimise Heating Load EUI (Vol) | Minimise Heating EUI (kWh/M3Volume Heated/Year)
| Maximise Lighting Efficiency | Lighting Efficiency (Lux/Watt)
Water | Minimise Lighting EUI | Lighting EUI (kWh/M2/Year) | 1 | 1 | 1 | 1 |  | 1 | 1 | [7 empty] | 1 | Water Meter | m3 | 1 Minute
|  |  | 1 | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Utiltiy Bill (Cost) | Euro | 1 Minute
|  |  | 1 | [14 empty] | Sum of Individual Water Meters | m3 | 1 Minute
| Minimise Air Flow | Total AHUs Air Flow (M3)
Catagories | Minimise Total AHUs Specific Power | Total AHU's Specific Power (kW)
Cooling |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Total Electrical Plant Cooling | kW | 1 Minute |  | Using these categories, a comprehensive understanding of performance can be established. If sub hourly measurements are taken for these categories then a further level of understanding can be attained.
[18 empty] | Chilled Plant Supply Temp | oC | 1 Minute |  | Without this type of breakdown, it may be impossible for a building manager to establish where energy is consumed. Baseline energy consumption values could be established for each criterion and compared with normal operating energy consumption values. | Dupllicate Measurement Refer to chiller
[18 empty] | Chillers Return Temp | oC | 1 Minute |  |  | Duplicate meaurement refer to chiller
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute |  |  | Dupllicate Measurement Refer to chiller
| Plug Load Electricity Use | Electricity Use (kWh) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[18 empty] | Chilled Plant Flow rate | m3 | 1 Minute |  | Further breakdown of cooling energy consumed would require meters for the chillers total electricity and for the total cooling towers/condensers electricity. These readings would enable further understanding of operational characteristics. | Dupllicate Measurement Refer to chiller
| Minimise People Mover Elec | People Mover Energy Use (kWh) | [15 empty] | Chiller water pumps elec | kWh | 1 Minute |  |  | Dupllicate Measurement Refer to chiller
[18 empty] | Cooling Towers Elec | kWh | 1 Minute |  |  | Dupllicate Measurement Refer to Cooling Tower
| Minimise Storey Elec Consumption | Storey Electrical Consumption (kWh)
Heating | Maintain Zone Temp | Zone Temperature (oC) | [15 empty] | Sum Gas (Boilers) | m3 | 1 Minute |  | Further breakdown of the heating energy consumed would require meters for the total boilers gas consumption and the total for electrical heating. These readings would enable further understanding of operational characteristics. | Duplicate measurement refer to Heating System
[18 empty] | Heating System flow rate | m3 | 1 Minute |  |  | Duplicate measurement refer to Heating System
| Maintain Zone Humidity | Zone Humidity (%) | [15 empty] | Heating System Supply Temp | oC | 1 Minute |  |  | Duplicate measurement refer to Heating System
| Monitor Air Velocity | Zone Air Velocity (m/s) | [15 empty] | Heating System Ret Temp | oC | 1 Minute |  |  | Duplicate measurement refer to Heating System
| Maintain Thermal Comfort Critera | Predicted Mean Vote (PMV) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute |  |  | Duplicate measurement refer to Heating System
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute |  |  | Duplicate measurement refer to Heating System
| Monitor Zone Integrity | Zone Integrity Signal (Windows and Doors Closed??) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Building Area Heated | m2 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Total Electrical Heating | kWh | 1 Minute
| Monitor Zone Occupancy | Zone Occumpancy Level (No of People)
Lighting | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Sum Lighting Sub Meters | kWh | 1 Minute |  | Further breakdown of the lighting energy consumed would require meters for the total zone lighting load, total outdoor lighting load and total electrical lighting load. These readings would establish if outdoor lighting is running during the day and if zone lighting was being used when the building is not occupied.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Sum Zone Lighting Meters | kWh/M2/Year | 1 Minute
| Minimise Air Sys Energy Use | Sys Energy Consumption (kWh) | [15 empty] | Outdoor Lighing Sensor | Lux | 1 Minute |  |  | Duplicate measurement refer to Site
| Minimise AHU Total Power | Air Handler Total Power (Supply and Return) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Emergency Lighting Elec Meter | kWh | 1 Minute
Ventilation | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Sum Systems Cumulative Flow Rate | m3 | 1 Minute |  | Total Ventilation electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
| Minimise AHU Specific Power | AHU Specific Power (kW/M3) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Sum AHU's Power | kW | 1 Minute
| Minimise Air Sys EUI | Sys EUI (kWh/M2) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Sum AHU's Energy | kWh | 1 Minute
| Minimise Daily AHU Elec | Daily Total AHU Electrical Usage (kWh)
| Minimise Daily Total AHU Volume | Daily Total AHU Volume (M3)
| Minimise Peak AHU Volume | Daily Maximum AHU Volume (M3)
| Minimise Daily Average AHU Power | Daily average Total AHU System Specific Power (kWh)
| Compare Air Flow and Outdoor DB | Daily Average Outdoor DB V Total Air Flow
Water Services | Monitor OA Temp Fraction | Outside air temperature fraction (Decimal) | [8 empty] | 1 | [6 empty] | Total Water Services Electricity | kWh | 1 Minute |  | Total Water Services electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
| Monitor OA Damper Fraction | OA Damper Fraction | [8 empty] | 1
Plug Loads | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Total Plug Loads Elec Meter | kWh | 1 Minute |  | Total plug loads electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
People Movers | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Total People Movers Elec meter | kWh | 1 Minute |  | Total people movers electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Compressed Air | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Total Compressed Air Elec Meter | kWh | 1 Minute |  | Total compressed electricity consumption is required to establish the breakdown of electrical consumption within a building. Enhanced resolution of energy consumption can assist energy management decision making and clarify operational characteristics.
Renewables | [5 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Total Renewables Elec Meter | kWh | 1 Minute |  | This measurement enables an overview of renewable system performance. It is a cumulative reading for solar thermal, photovoltaic and wind generated electricity respectively. These measurements enable a rapid evaluation of renewable technology performance. Without these measurements post operational evaluation is not achievable for these components.
[7 empty] | 1 | [10 empty] | Total Renewables Heat Meter | kWh | 1 Minute
Building Tennant | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Tennant Elec Sub Meter (kWh) | kWh | 1 Minute |  | A building story electrical meter is included in the generic set of measurements to account for building tenants that may occupy an individual floor. It is unrealistic to apportion building energy consumption any other way.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Tennant Gas Sub Meter (m3) | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Tennant Gas Sub Meter (m3) | m3 | 1 Minute
Zone | Minimise Fan Energy Consumption | Fan Energy Consumption (kWh) |  | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Temp | oC | 1 Minute |  | In normal office environments temperature is the key variable required. Zones containing art work or swimming pools may require tight humidity control. If zones are occupied then an energy manager requires the appropriate data stream that reflects this. Where possible zones should not be conditioned unless occupied or have strict indoor environmental requirements. An occupancy level can be used for comparison with zone plug loads and zone lighting levels and also helps establish micro-zones. A door/window closed signal would enable automatic shut off of air conditioning systems if a door or window was open. This measurement should be included for each aperature. Metabolic rate and air velocity are required for naturally ventilated spaces. Mean radiant temperature is required for zones with under floor heating of chilled beams. Zone lux levels are required where day lighting strategies are incorporated.
| Minimise VFD Speed Signal | VFD Fan Signal (Hz) |  | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Temp Setpoint | oC | 1 Minute
| Maximise Fan Efficiency | Fan Efficiency (%) |  | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Relative Humidity | % | 1 Minute
| Monitor Fan Hours of Use | Hours Run (Must Find Out) |  | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Relative Humidity Setpoint | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 |  | 1 |  |  | 1 | 1 |  | 1 | Occupancy Signal (CO2or PIR) | CO2 PPM | 1 Minute
[6 empty] | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Air Velocity | m/s | 1 Minute |  |  | Especially for naturally ventilated spaces
|  |  |  | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Zone Mean Radiant Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 |  | 1 |  |  |  | 1 |  | 1 | Metabolic Rate | w/m2 | 1 Minute |  | From a Table
| Minimise Heating Energy use | Heating Energy Use (kWh) |  |  |  | 1 |  | 1 | 1 | [5 empty] | 1 |  | 1 | Doors/Windows Closed (Yes/No) | Yes/No | 1 Minute |  | For Each Door/Window
| Maximise Heating Efficiency | Heating Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Magnitude of opening for each door or window | % | 1 Minute |  | Only where natural ventilation is used.
| Minimise Cooling Energy Use | Cooling Energy Use (kWh) |  |  |  | 1 |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | Zone Lux Level | Lux | 1 Minute | 1
| Maximise Cooling Efficiency | Cooling Efficiency (%) |  |  |  | 1 |  | 1 | 1 |  |  |  |  | 1 |  |  | 1 | Zone Occupancy | People | 1 Minute
[6 empty] | 1 |  | 1 | 1 |  |  |  |  | 1 |  | 1 | 1 | Zone Lighting load | kWh | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Zone Plug Load | kWh | 1 Minute
SYSTEMS | [19 empty] | 1 Minute
Air System | Maintain Setpoint | Mixing Box Setpoint (TempoC,(%) Humidity, Enthalpy kJ/kg) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Total Air System Elec | kWh | 1 Minute |  | The system supply air temperature, flow rate and serviced zone temperatures are key indicators of system performance. If the supply temperature and zone conditions are not satisfying their setpoint, then the system is not performing. These are critical measurements.
| Monitor Mixing Box Damper Position | Mixing Box Damper Position (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Fan Elec (kWh) | kWh | 1 Minute |  | Duct static pressure may be used when diagnosing problems with maintaining Setpoints.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | System On/Off Signal |  | 1 Minute |  | The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | System On/Off Status |  | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Fan Elec | kWh | 1 Minute |  | Other measurements are duplicated by the components
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Each Component Elec(kWh)/Area | kW | 1 Minute
[6 empty] | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | AHU Flow rate | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Zones Temps | oC | 1 Minute |  |  | Duplicate measurement.Included for each zone object
[6 empty] | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | MixA Temp | oC | 1 Minute
[18 empty] | OA Temp | oC | 1 Minute |  |  | Duplicate measurement refer to site
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | Supply Air Temperature | oC | 1 Minute
| Maximise Energy Transfer | Air To Air HR Energy Transfer Rate (kW) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Duct Static Pressure | Pa | 1 Minute
| Maximise Efficiency | Air to Air HR Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | OA Air Damper Position | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | OA Damper Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Damper Position | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Damper Control Signal | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply RH Setpoint | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Mix Air RH | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outside Air RH | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air RH | % | 1 Minute
| Maximise Energy Transfer | Air To Air HR Energy Transfer Rate (kW) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Relative Humidity | % | 1 Minute
| Maximise Efficiency | Air to Air HR Efficiency (%)
Natural Ventilation System | [17 empty] | Wind Speed | m/s | 1 Minute |  | The critical measurement for this system type is the zone temperature. This measurement over a 24 hour period could influence system start up (opening times) and night ventilation strategies. | Duplicate measurement refer to site
[18 empty] | Wind Direction | Degrees | 1 Minute |  | For evaluation of a natural ventilation system, air velocity in the zone and at apertures must be recorded. Pressure at the windward and leeward façade would aid diagnostics. Aperture opening percentage is also required for system evaluation. | Duplicate measurement refer to site
[18 empty] | Zone Temperature | oC | 1 Minute |  |  | Duplicated Measurement refer to zone
[18 empty] | Window Percentage Open | % | 1 Minute |  |  | Duplicate measurement.Included for each zone object
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Zones Temps | oC | 1 Minute |  |  | Duplicate measurement.Included for each zone object
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Zone Temp Setpoint | oC | 1 Minute |  |  | Duplicate measurement.Included for each zone object
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Natural Ventiation Power | kWh | 1 Minute |  | Included to determine the net benefit of natural ventilation systems
[6 empty] | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | Pressusre at Windward Façade | Pa | 1 Minute |  |  | Duplicate oBject at Site Level
[6 empty] | 1 |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 1 | Pressusre at Leeward Façade | Pa | 1 Minute
Fan | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fan Elec meter | kWh | 1 Minute |  | The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to. Without these measurement streams each fan could operate when not required or consume excessive energy during normal operation. Duct static pressure may be required as a monitor of performance. Electricity meter would be a supplemental measurement and would be the lowest level of electrical consumption.
| Maximise Heat Pipe Efficiency(Sensible Only) | Heat Pipe Efficiency (%) | [15 empty] | Air Flow Rate | m3 | 1 Minute |  |  | Duplicate measurement refer to air system
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fan VFD Signal Meter | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Duct Total Pressure | Pa | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fan Inlet Pressure | Pa | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fan Outlet Pressure | Pa | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
Fan Coil Unit | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | The supply temperature is the critical measurement for this component. The effectiveness of the component can be monitored if zone temperature is compared with supply temperature. Unit operation can be determined by comparing outside air temperature and supply temperature. The control signal and operational status are also required to ensure the fans are operating as intended when they are supposed to. Component diagnostics could be performed using additional streams (air flow rate, water flow rate, water inlet and outlet temperatures). If heating is added by an electrical element this should be included as a separate meter.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air flow rate | m3 | 1 Minute |  | An electricity meter would be a supplemental measurement and would be the lowest level of electrical consumption.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | If water based heating cooling same measurements for water side | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fan Elec | kWh | 1 Minute
| Minimmise Humidificaion Load | Humididfication Load (kg/hour) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status Signal | % | 1 Minute
Mixing Box | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Mixed Air Temp | oC | 1 Minute |  | The key measurement stream for this component is outlet temperature (compared with setpoint). If enthalpy control is used then the relative humidity and temperature are required for the outside air, return air and supply air streams. These measurement streams allow diagnosis of the mixing box component which if not operated properly can result in excessive energy consumption. Further diagnostics require the return and fresh air damper operational status and control signals are required. The supply air flow rate is also necessary. Without these measurements it is impossible to quantify and evaluate performance.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Mixed Air relative humidty | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Maximise Performance Efficicency | Humidifier Efficicency (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Humidity Setpoint | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Relative Humidity (%) | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Damper Position Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Damper position sensor | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outside Air Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outside Air Relative Humididty | % | 1 Minute |  | If enthalpy control is used | Duplicate Measurement Refer to Site
| Control Supply Temperature | Supply Air Temperature (oC) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Outside Air Flow rate | (m3/s) | 1 Minute
| Control Supply Air Velocity | Supply Air Velocity (M3) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
| Control Air Flow Rate | Supply Air Flow Rate (M/S) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Flow rate | (m3/s) | 1 Minute
| Control Pressure | Duct Pressure (Pa)
Air to Air Heat Rec | Contol Humidity | Supply Air Relative Humidity (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | The objective of this component is to maximize the heat recovered from the return air stream. Outside air and the temperature of the air leaving the component give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply air flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity | % | 1 Minute
| Mimimise Elec Consumption | Elec Use (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
| Monitor Hours of Use | Hours of Use (Hours) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Return in temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
| Maintain Supply Temperature | Supply Air Temperature (oC) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity | % | 1 Minute
| Maintain Supply Air Flow Rate | Supply Volumetric Flow Rate (M3/S) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Maintain Supply Air Humdidty | Supply Air Humidity (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
Wheel | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | The objective of this component is to maximize the heat recovered from the return air stream. Outside air and the temperature of the air leaving the component give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Same as 6101 |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Humidity Setpoint | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply air flow rate | (m3/s) | 1 Minute |  | Thermal wheels are prone to leaks and performance evaluation of such units should be undertaken where possible.
| Same as 4401 |  |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Humidity Ratio | kg/kg | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Humidity Ratio | kg/kg | 1 Minute
| Maximise Effectiveness | kWh per Nominal meters cubed(kWh/Nm3) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Return in temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Humidity Ratio | kg/kg | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Humidity Ratio | kg/kg | 1 Minute
| Minimise Chiled Plant Power | Total Chillers Power |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
| Minimise Chilled Plant Output | Total Chillers Output |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status Signal | % | 1 Minute
Heat Pipe | Monitor Chilled Plant Heat of Rejection | Total Chilled Water Plant Heat of Rejection (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | The objective of this component is to maximize the heat recovered from the return air stream. The inlet and outlet temperatures give an energy manager an indication of performance. To determine heat recovered and the efficiency of the heat recovery unit all additional measurements are required.
| Monitor Chill Water Plant Heat Balance | Chilled Water Plant Heat Balance (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Humidity Setpoint | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply air flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return in temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status Signal | % | 1 Minute
| Minimise Chiller Energy Use | Chiller Energy Use (kW)
Humidifier | Maximise Chiller COP | COP (Decimal Value) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | The critical measurement required for a humidifier is the outlet air relative humidity and temperature. Performance evaluation of the humidifier requires quantity of steam of sprayed water released to the supply air, the humidity ratio, temperature of the supply air and the humidity ratio of the outlet air. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to.
| Monitor Chiller Load V Outdoor DB | Daily Average Outdoor DB V Daily Chiller Load |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
| Monitor Chiller Hours of Use | Hours of Use (Hours) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply air flow rate | (m3/s) | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Humidity Setpoint | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity | % | 1 Minute
| Maximise Cooling Tower Heat Rejected | Cooling Tower Heat Loss (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Make Up Water | l/hour | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
|  | 3501 |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status Signal | % | 1 Minute
Dehumidifier | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in temp | oC | 1 Minute |  | See cooling coil but must be accompanied by a heating coil
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply air flow rate | (m3/s) | 1 Minute
| same as above |  |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply in Relative Humidity (%) | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Out Relative Humidity | % | 1 Minute
| Monitor Condenser Loop Load | Plant Condenser Loop Thermal Load (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status Signal | % | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
Diffuser | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature | oC | 1 Minute |  | The supply temperature is the key measurement for a diffuser. In certain circumstances the relative humidity of the supply air is also required. Air velocity and duct static pressure may be required if supply temperature is not satisfactory or there are occupant complaints due to drafts. The control signal and operational status are also required to ensure the diffuser dampers are operating as intended when they are supposed to. | Duplicate Measurement refer to Air System
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Velocity |  | 1 Minute
| Refer to 6201 |  |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Flow Rate | (m3/s) | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Minimise Required Energy Transfer Rate | Cooling Coil Energy Use (kWh) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Maximise Efficiency | Cooling Coil Efficiency (%)
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Duct Air Pressure |  | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Humidity | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Actuator Position | % | 1 Minute
FumeHood | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fume Hood Elec Meter | kWh | 1 Minute |  | The critical measurement here is an indicator of if an experiment is in progress or not. Combined with the on/off status optimum operation can be achieved. The electrical meter on the fume hood would be required to quantify electrical energy consumption. It is not a critical measurement.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Monitor Cold Storage Transfer In | Cold Storage Energy Transfer (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | On/Off Status | % | 1 Minute
| Monitor Cold Storage Use (OUt) | Cold Storage Energy use (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Experiment In Progress | Yes/No | 1 Minute
| Maximise Cold Storage Efficiency | Cold Storage Efficiency (%)
Dual Duct Box | [17 empty] | Zone Temp | oC | 1 Minute |  | The key measurement stream for this component is supply temperature (compared with setpoint). For component diagnostics the Hot and cold damper operational status and control signals are required. The supply air flow rate is also necessary. Without these measurements it is impossible to quantify and evaluate performance. | Duplicate Measurement Refer to Zone
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temp | oC | 1 Minute |  |  | Duplicate Measurement Refer to Air System
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Hot Damper | % | 1 Minute
| Minimise Energy Consumption | Energy Consumption (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Cold Damper | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Air Flow Rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal hot Damper | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal Cold Damper (%) | % | 1 Minute
[18 empty] | Supply Temp Setpoint | oC | 1 Minute |  |  | Value but not a measurement
Heating Coil | [22 empty] | Duplicate Object contained in Air System
| Maximise Saturation Effectiveness | Saturation Effectiveness (%)
Cooling Coil | [22 empty] | Duplicate Object contained in Air System
Compressed Air | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elec In | kWh | 1 Minute |  | The important variables for evaluating the performance of a compressed air system are the Electricity in and the volume of air produced. The control signal and operational status are also required to ensure the compressed air system is operating as intended when it is supposed to.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Nominal Air Volume Produced | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | On/Off Status | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Signal | % | 1 Minute
Chilled Plant | Maximise Saturation Effectiveness | Saturation Effectiveness (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Cooling Plant Elec |  | 1 Minute |  | This level of measurement is required for large installations with more than one plant component used for cooling. The Electricity total is an aggregation of the individual components consumption. However this should be its own individual measurement to ensure consistency within the system as a whole. | These measurments may be applied to individual heating plant if required in a smaller building
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Chilled Water Plant Supply out temp | oC | 1 Minute |  | The chilled plant cooling output (flow rate, inlet and outlet fluid temperatures) is also required to deliver an overall efficiency. For plant maintenance the condenser circuit also requires monitoring. Flow rate, inlet and outlet fluid temperatures are required to determine the heat rejected by the overall chilled plant system.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Chilled Water Plant Supply in temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Demand Flow Rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Sum Condenser Loops Load | kWh | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Condenser Loops out temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Condenser Loops in temp | oC | 1 Minute
| Maximise System Efficiency | Roof Spray System Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Condenser Loops Flow Rate | (m3/s) | 1 Minute
| Minimise Energy Use | Pump Electricity Use (kWh)
Secondary Chilled Water Loop | Mimimise Make Up Water | Volume of Make up Water | [15 empty] | Primary Circuit Water Inlet Temp | oC | 1 Minute |  |  | Duplicate Measurement refer to Chilled Plant
[18 empty] | Mains Water Temperature | oC | 1 Minute |  |  | Duplicate Measurement refer to Utility 'Water'
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Secondary Circuit Water Flow Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Secondary Circuit Return Water Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Secondary Circuit Water Flow rate | (m3/s) | 1 Minute
| Minimise Heating System Output | Total Boilers Output |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Primary Circuit Water Flow Rate | (m3/s) | 1 Minute
| Minimise Heating Fuel Consumption | Total Boilers Gas Flow |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Valve Open | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
Chiller | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elec Meter | kWh | 1 Minute |  | The electricity consumed and cooling delivered (flow rate, inlet and outlet water temperatures) are essential measurements for this component. A coefficient of performance can be determined from these values.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute |  | The flow temperature alone is also a key indicator of how the chiller is conforming to design intent. The control signal and operational status are also required to ensure the boiler is operating as intended when it is supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute |  | For plant maintenance the condenser circuit also requires monitoring. Flow rate, inlet and outlet fluid temperatures are required to determine the heat rejected by the condenser loop.
| Maximise Boiler Efficiency | Boiler Efficiency (%), Boiler Runtime (Hours) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Minimise Boiiler Gas Flow | Total Boiler Gas Flow |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Monitor Boiler Gas V Outdoor DB | Daily Average Outdoor DB V Daily Boiler Load |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute
| Monitor Daily Gas Consumption | Maximum Daily Total Boiler Heating Energy |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | On/Off Status | % | 1 Minute |  | Hours run meter is required for standard maintenance.
| Monitor Boiler Hours of Use | Hours of Use (Hours) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Hours Run Meter |  | 1 Minute
Cooling Tower |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Refrigerant Supply Temp | oC | 1 Minute |  | The cooling tower heat rejected is of primary importance (Refrigerant Supply, ret temp, Condenser Circuit Flow Rate). These measurements when combined with cooling load delivered should illustrate chiller operation. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to. Outside air temperature is also an important indicator of heat rejection potential. Water cooled cooling towers also require wet bulb temperature of the air and volume of water used. Efficiency can be calculated using these measurement streams.
| Maximise Total PV Production | Total PV System Production (kWh/Time Period) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Refrigerant Return Temp | oC | 1 Minute
| Maximise Net PV Production | Net PV System Production (kWh/Time Period) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Condenser Circuit Flow Rate | m3 | 1 Minute |  | The hours run meter is required for standard maintenance.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Make Up Water Flow Rate (If water Cooled) |  | 1 Minute
| Maximise Equivalent Annual Hours | Equivalent Annual Hours Peak PV Product(hrs/yr/kWp) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Maximise Offset Facility Elec Load | Facility Electrical Load Offset by PV Production (%) |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Maximise Offset Facility Total Load | Facility Total Energy Load Met by PV Production (%) |  |  |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Operational Signal | % | 1 Minute
| Monitor Total Elec Exported | Total Electricity Exported to Utility (kWh/Time) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Status | % | 1 Minute
| Monitor Total Incident Solar | Total Incident Solar Radiation (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Hours Run Meter | Hours | 1 Minute
| Maximise PV Effectiveness | PV System AC Electricity Generation Effectiveness (%)
Humidifier | Maximise PV Performance Ratio | PV System Performance Ratio (%) | [20 empty] | Duplicate Object contained in Air System
| Minimise Net Facility Energy Use | Net Facility Electricity Use (kWh/Time)
Condenser | Minimise Peak Elec Demand | Peak Demand of Net Facility Electricity Use(kW/Time ) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Refrigerant Supply temp | oC | 1 Minute |  | The condenser loop load is of primary importance (Refrigerant Supply, ret temp, Condenser Circuit Flow Rate). These measurements when combined with cooling load delivered should illustrate chiller operation. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to. Outside air temperature and make up water used are also an important indicator of heat rejection potential. Water cooled condensers also require wet bulb temperature of the air. Efficiency can be calculated using this measurement stream.
| Mimimise Total Peak Demand | Peak Demand of Total Facility Elec Use without PV(kW) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Refrigerant return temp | oC | 1 Minute
| Maximise Peak Demand Reduction | Reduction of Peak Demand because of PV system (kW) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Condenser Circuit Flow Rate | m3 | 1 Minute
| Minimise Elec Costs | Facility Electricity Costs without PV System (Currency) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Maximise PV Energy Cost Savings | Energy Cost Savings Resulting from PV System(Currency) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Maximise Average PV Production | Maximum Time-Series Net PV Production (kW/Time) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
| Maximise Daily Average PV Product | Average Daily Time-Series PV Production (kW V time) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
[18 empty] | Hours Run Meter |  | 1 Minute
Pump | Maximise Solar Water Heating | Solar Water Heating Delivered (kWh) | [17 empty] | 1 Minute |  |  | Duplicate Object Contained in Hot Water Systems
| Maximise Solar Water Efficiency | Solar Water Heating Efficiency (%)
Cooling Coil | Maximise Solar % of Total Heating | Percentage of Total Heating (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Air Inlet Temperature | oC | 1 Minute |  | The Valve operational status and control signal are critical measurements for a heating coil. The air side outlet temperature can be compared with a setpoint to determine coil effectiveness. If the operational status and control signal measurements are absent then ineffective coil operation cannot be identified.
| Maximise Savings | Resultant Energy Savings (Unito of Local Currency) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Air Outlet Temperature | oC | 1 Minute |  | For component diagnosis the flow rate, inlet and outlet temperatures are required for both the air and water side. Fouling can be identified by quantifying efficiency over an extended time period.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Air Flow Rate |  | 1 Minute
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute
| Maximise Furnace Efficiency | Furnace Efficiency (%) |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Minimise Furnace Energy Use | Furnace Energy Output (kW) |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Minimise Furnace Gas Flow | Total Furnace Gas Flow |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute
| Monitor Furnace Gas V Outdoor DB | Daily Average Outdoor DB V Daily Furnace Load |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Coil Valve | % | 1 Minute
| Monitor Daily Gas Consumption | Maximum Daily Total Furnace Heating Energy |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Coil Valve Signal | % | 1 Minute
Thermal Storage | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply temp (oC) IN | oC | 1 Minute |  | Cooling output (flow rate, inlet and outlet fluid temperatures) is the key measurement required for a thermal storage system. Efficiency of the system and thermal losses are determinable using these datum streams. The control signal and operational status are also required to ensure the thermal storage unit is operating as intended when it is supposed to. The supply temperature out is a direct measure of the storage temperature.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Flow rate (Water) IN (m3/s) | (m3/s) | 1 Minute
| Maximise CHP Efficiency | CHP Total Efficiency (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply temp (oC) Out | oC | 1 Minute
| Monitor Elec Production | CHP Elec Production (kWh) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Monitor Elec Production Efficiency | CHP Elec Efficiency (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
| Monitor Heat Production | CHP Heat Production (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Flow rate (Water) Out (m3/s) | (m3/s) | 1 Minute
| Monitor Heat Production Efficiency | CHP Heat Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Signal (%) | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Status (%) | % | 1 Minute
Chilled Beam | [17 empty] | Mean Radiant Temp(oC) | oC | 1 Minute |  | Flow rate, inlet and outlet temperatures can be combined to deliver a cooling output of the chilled beam circuit. This cooling output can help establish the distribution of cooling within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of cooling used. The mean radiant temperature of the space is key objective when using this type of system. | Duplicate Measurement contianted in Zone Object
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Inlet Temp (oC) | oC | 1 Minute
| Opearation History | Time (%) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Outlet Temp (oC) | oC | 1 Minute
| Maximise COP | COP (Decimal Value) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow rate (m3/s) | (m3/s) | 1 Minute
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Valve Open (%) | % | 1 Minute
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Valve Signal (%) | % | 1 Minute
Direct Evap Cool | [5 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Inlet DB Temperature | oC | 1 Minute |  | The key variables are water flow rate (cost) and supply outlet dry bulb temperature. These variables indicate system performance. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to.
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Outlet DB Temperature | oC | 1 Minute
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Return(In WB) | oC | 1 Minute |  | Measurements required for efficiency of the indirect cooling include supply inlet temperature. Return inlet wet bulb, supply and return air flow rates. Careful monitoring of efficiency can result in lower operating costs.
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Minimise DHW Use | DHW Load (KWh) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Air Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
| Minimise Required Energy Transfer Rate | Heating Coil Energy Use (kW)
Indirect Evap Cool | Maximise Efficiency | Heating Coil Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Inlet DB Temperature | oC | 1 Minute |  | The key variables are water flow rate (cost) and supply outlet dry bulb temperature. These variables indicate system performance. The control signal and operational status are also required to ensure the indirect evaporative cooling unit is operating as intended when it is supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Outlet DB Temperature | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return(In WB) | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Air Flow rate | (m3/s) | 1 Minute |  | Measurements required for efficiency of the indirect cooling include supply inlet temperature. Return inlet wet bulb, supply and return air flow rates. Careful monitoring of efficiency can result in lower operating costs.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Return Air Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow rate | (m3/s) | 1 Minute
| Maximise Efficiency | Pump Efficiency (%) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
| Minimise Energy Use | Pump Energy Use (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
| Monitor Pump Hours of Use | Hours of Use (Hours)
Roof Spray System | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Pump Elec | kWh | 1 Minute |  | Night sky temperature (measured at the site level) gives an overview of cooling potential.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Make up Water Volume | m3 | 1 Minute |  | The electrical consumption and the volume of water added to the system are key variables. These are energy and cost inputs. The outlet temperature from the roof, the outlet valve status and the outlet valve control signal are required to monitor operation. Adding the temperature of the return water and the water flow rate measurements illustrate how the cooling achieved by the night sky system.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Inlet Temp to roof | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outlet Temp from roof | oC | 1 Minute
| Monitor Water Temp | Water Temp (Degrees C) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Valve Open | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
Heating System |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Heating Plant Gas Meters | m3 | 1 Minute |  | This level of measurement is required for large installations with more than one plant component used for heating. The gas consumed total is an aggregation of the individual components consumption. However this should be its own individual measurement to ensure consistency within the system as a whole. | These measurments may be applied to individual heating plant if required in a smaller building
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Heating Plant Flow rate | l/s | 1 Minute |  | The heating plant heat output (flow rate, inlet and outlet water temperatures) is also required to deliver an overall efficiency.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
| Minimise Energy Consumption | Energy Consumption (kWh) |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Heating Plant Supply Temp In | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Heating Plant Supply Temp Out | oC | 1 Minute
Secondary Hot Water Loop | [22 empty] | Duplicate Object Same as Secondary Chilled Water Loop
Boiler | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Boiler Gas | m3 | 1 Minute |  | The boiler fuel consumed and heat output (flow rate, inlet and outlet water temperatures) are essential measurements for this component. The flow temperature alone is also a key indicator of how the boiler is conforming to design intent. The control signal and operational status are also required to ensure the boiler is operating as intended when it is supposed to.
| Minimise Energy Consumption | Energy Consumption (kWh) |  |  |  | 1 |  | 1 | 1 | [7 empty] | 1 | Inlet Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outlet Temp | oC | 1 Minute |  | Hours run meter is required for standard maintenance.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | On/Off Status | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Boiler Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Hours Run Meter |  | 1 Minute
| Minimise Elevator Electricity | Energy Use (kWh)
Solar Photovoltaic |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | PV Elec Meter | kWh | 1 Minute |  | Solar radiation and electricity produced are the key measurements for PV panels. The control signal is also an essential measurement as electricity is needed instantly if required.
[6 empty] | 1 | 1 | 1 | 1 | [7 empty] | 1 | Solar Radiation | kWh | 1 Minute |  | If these readings are absent. Excessive electricity may be purchased from the grid resulting in higher costs. Also peak power required from the grid may be increased with the potential for further higher tariffs. | Duplicate measurement refer to Site
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
1 Minute
| Minimise Escalator Electricity | Energy Use (kWh) | [16 empty] | % | 1 Minute
[19 empty] | % | 1 Minute
[19 empty] | kWh/Time | 1 Minute
[19 empty] | kWh | 1 Minute
[19 empty] | % | 1 Minute
| Minimise Walkway Electricity | Energy Use (kWh) | [16 empty] | % | 1 Minute
[19 empty] | kW | 1 Minute
[19 empty] | kW | 1 Minute
[19 empty] | kW | 1 Minute
[19 empty] | kW | 1 Minute
[19 empty] | Euro | 1 Minute
1 Minute
[19 empty] | kW | 1 Minute
[19 empty] | kW | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
Solar Water Heater | [17 empty] | Solar Radiation | kWh | 1 Minute |  | Solar radiation and heat delivered (flow rate, inlet and outlet water temperatures) to the hot water are key measurements here. Combined they deliver the effectiveness and efficiency of the system. The flow temperature is required on its own as if a system limits are exceeded catastrophic failure can occur. The control signal and operational status are also required to ensure the solar water heater is operating as intended when it is supposed to. | Duplicate Measurement refer to Site
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 | 1 | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Valve Open | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
Furnace | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Furnace Gas Meter | (m3/s) | 1 Minute |  | Fuel consumption and heat output (flow rate, inlet and outlet water temperatures) are critical measurements. Overall unit efficiency and energy consumption can be determined using these measurements. The control signal and operational status are also required to ensure the furnace is operating as intended when it is supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute |  | If any of these datum streams are absent then the unit has the potential to operate inefficiently.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute |  | Hours run meter is required for standard maintenance.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
[18 empty] | Hours Run Meter | Hours | 1 Minute
CHP | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Fuel Meter | (m3/s) | 1 Minute |  | Fuel consumption, heat output (flow rate, inlet and outlet temperatures) and electricity produced are critical measurements. Overall unit efficiency and energy consumption can be determined using these measurements. The control signal and operational status are also required to ensure the CHP unit is operating as intended when it is supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elec Output | kWh | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | (m3/s) | 1 Minute |  | If any of these datum streams are absent then the unit has the potential to operate inefficiently.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute |  | Hours run meter is required for standard maintenance.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Electriciyt Output Setpoint | kWh | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Hours Run Meter | Hours | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
Heat Pump | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elec Meter | kWh | 1 Minute |  | Electricity input is a key measurement for a building manager. The control signal and operational status are also required to ensure the heat pump is operating as intended when it is supposed to.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply side Water Inlet Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Side Water Outlet Temp | oC | 1 Minute |  | Fluid flow rate, inlet and outlet temperatures for the supply and demand sides are required to determine the coefficient of performance for a heat pump. Without these measurements it is impossible to determine if the heat pump is operating as it was intended to.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Side Water Flow Rate | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Demand side Water Inlet Temp( | oC | 1 Minute |  | Hours run meter is required for standard maintenance.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Demand Side Water Outlet Temp | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Demand Side Water Flow Rate | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Hours Run Meter | Hours | 1 Minute
DHW |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute |  | The critical measurements for this circuit are flow temperature (to avoid burning), return temperature and flow rate. Combined these measurements also deliver the heat delivered to the domestic hot water circuit. This reading is required to understand the end use of heat in the building.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute |  | If the flow rate is absent leaks or dripping taps may go unnoticed.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | DHW Valve | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
Heating Coil | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Air Inlet Temperature | oC | 1 Minute |  | The Valve operational status and control signal are critical measurements for a heating coil. The air side outlet temperature can be compared with a setpoint to determine coil effectiveness. If the operational status an control signal measurements are absent then ineffective coil operation cannot be identified.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Air Outlet Temperature | oC | 1 Minute |  | For component diagnosis the flow rate, inlet and outlet temperatures are required for both the air and water side. Fouling can be identified by quantifying efficiency over an extended time period.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Air Flow Rate | m3 | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Inlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Outlet Temp | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Water Flow Rate | m3 | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Coil Valve | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Coil Valve Signal | % | 1 Minute
Pump | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Flow meter | l/s | 1 Minute |  | Electrical meter for all pumps. The flow meter, inlet and outlet pressures, operational status and control signal are all required for advanced diagnostics. These are more useful for pumps with a variable speed drive.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elec meter | kWh | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Inlet Total Pressure | Pa | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Outlet Total Pressure | Pa | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Pressure Setpoint | Pa | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | On/Off Status | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Pump Control Signal | % | 1 Minute
Water Storage |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Tank Water Temperature (oC) | oC | 1 Minute |  | Maintaining the tank water temperature is the key objective here. It is a critical measurement.
[18 empty] | Supply Circuit Inlet Temp | oC | 1 Minute |  | Advanced diagnostics require quantification of heat in and heat out of the water tank. Flow rate, Inlet and outlet temperature are required for both the demand and supply circuits. Without these measurements it is impossible to determine heat losses from the tank.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Storage Temperature Setpoint | oC | 1 Minute
[18 empty] | Supply Circuit Outlet Temp | oC | 1 Minute
[18 empty] | Supply Circuit Flow rate | (m3/s) | 1 Minute
[18 empty] | Demand+D2 Circuit Inlet Temp | oC | 1 Minute
[18 empty] | UFH Circuit Outlet Temp | oC | 1 Minute
[18 empty] | UFH Circuit Flow rate | (m3/s) | 1 Minute
Under Floor Heating |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | UFH Circuit Inlet Temp | oC | 1 Minute |  | Flow rate, inlet and outlet temperatures can be combined to deliver a heat output of the under floor heating circuit. This heat output can help establish the distribution of heat within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of heat used. The mean radiant temperature of the space is key objective when using this type of system.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | UFH Circuit Outlet Temp | oC | 1 Minute |  | If these reading are combined with valve position and control signal then diagnostics can be performed on the circuit.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | UFH Circuit Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Mean Radiant Temperature | oC | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | UFH Circuit Valve Position | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | UFH Circuit Valve Position | % | 1 Minute
Radiator Circuit |  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Radiator Circuit Inlet Temp | oC | 1 Minute |  | Flow rate, inlet and outlet temperatures can be combined to deliver a heat output of the radiator circuit. This heat output can help establish the distribution of heat within a building. The inlet temperature on its own illustrates the flow temperature to the circuit but alone is not an indicator of heat used.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Radiator Circuit Oulet Temp | oC | 1 Minute |  | If these reading are combined with valve position and control signal then diagnostics can be performed on the circuit.
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Supply Temperature Setpoint | oC | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Raiator Flow rate | (m3/s) | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Radiator Circuit Valve Position | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Radiator Circuit Control Signal | % | 1 Minute
People Mover Sys | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Total People Movers Elec Meter | kWh | 1 Minute |  | This measurement on its own can identify where electricity is being used in a building, if it is a constant load throughout out the day or not and if people mover systems are running during unoccupied hours.
Elevator | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Occupancy (CO2) | PPM | 1 Minute |  | These measurement streams can determine the operation of an individual elevator system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Elevator Elect | kWh | 1 Minute |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
Escalator | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Occupancy (CO2) | PPM | 1 Minute |  | These measurement streams can determine the operation of an individual escalator system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Escalator Elec | kWh | 1 Minute |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute
Walkway | [5 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Occupancy (CO2) | PPM | 1 Minute |  | These measurement streams can determine the operation of an individual walkway system. The walkway electrical consumption is important. Operational performance can be determined using the 3 other measurement streams. Is the walkway operating when not required and is the walkway operating as it was intended to when it is required?
|  |  |  | 1 |  | 1 |  | 1 | 1 | [7 empty] | 1 | Operating Schedule | Time | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Walkway Elec | kWh | 1 Minute |  | If the control and occupancy streams are missing then optimum operation is not achievable. Performance evaluation over time is also not achievable if these streams are missing.
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Control Signal | % | 1 Minute
[6 empty] | 1 |  | 1 | 1 | [7 empty] | 1 | Operational Status | % | 1 Minute