## IdealSetPO&PM
Tag | Building Object | Performance Objective | Performance Metric | Per. Metric Unit | Datum Streams Required ; Units | Min Time | Calculations | From BMS | From Simulatiion | From Utility Provider
M1001 | Site | : Outdoor Dry Bulb Temp | Outdoor Dry Bulb Temp | oC | Outdoor Dry Bulb Temperature (oC) | 1 min | None Needed | Yes | Yes | No
M1002 | Site | : Outdoor Wet Bulb Temp | Outdoor Wet Bulb Temp | oC | Outdoor Dry Bulb Temperature (oC) | 1 min | None Needed | Yes | Yes | No
M1003 | Site | : Outdoor % Humidity | Outdoor Humidity | % | Outside Air Humididy (%) | 1 min | None Needed | Yes | Yes | No
M1004 | Site | : Average Daily Dry Bulb Temp | Average Daily Outdoor Temperature | oC | Outdoor Dry Bulb Temperature (oC) | 1 min | Sum Daily values/no of values | Yes | Yes | No
M1005 | Site | : Heating Degree Days | Heating Degree Days | Degree Days | Outdoor Dry Bulb Temperature (oC) | Daily | None Needed | Yes | Yes | No
M1006 | Site | : Cooling Degree Days | Average Daily Outdoor Temperature | oC | Outdoor Dry Bulb Temperature (oC) | Daily | None Needed | Yes | Yes | No
M1007 | Site | : Wind Speed | Wind Speed | m/s | Wind Velocity (m/s) | 1 min | None Needed | Yes | Yes | No
M1008 | Site | : Wind Direction | Wind Direction | Degrees | Wind Direction (Degrees) | 1 min | None Needed | Yes | Yes | No
M1009 | Site | : Total Incident Solar | Total Incident Solar Radiation | kWh | Solar Radiation (kWh) | 1 min | None Needed | Yes | Yes | No
M1010 | Site | : Available Natural Night | Available Natural Light | Lux | Natural Light Levels (Lux) | 1 min | None Needed | Yes | Yes | No
M1101 | Building | : Building Energy Use | Total Energy Use | kWh | Electricity Bills (Monthly Monetary Values) | 1 min | Sum (Utility Totals) | Yes | Yes | No
M1102 | Building | : Builidng EUI | Energy Use Intensity | kWh/m2/Year | Electricity Energy Consumption (kWh); Floor Area (m2) | Monthly | Sum Energy consumption/Area | Yes | Yes | No
M1103 | Building | : Builidng EUI | Energy Use Intensity | kWh/m3/Year | Electricity Energy Consumption (kWh); Building Volume (m3) | Monthly | Sum Energy consumption/Area | Yes | Yes | No
M1104 | Building | : Total Energy Cost | Total Energy Cost | Unit of Local Currency | Electricity Bills (10 minute price information) | 1 min | Sum(Energy*Price) per utility | Yes | Yes | Yes
1105 | Building | : Normalised atmospheric emissions | Normalised atmospheric emissions | Tons CO2 | Electricity bills (Monthly Consumption Values) | Monthly | Sum of CO2 Emissions | Yes | Yes | Yes
1106 | Building | : HVAC Energy Cost | Total HVAC Cost | Unit of Local Currency | Electricity Price Information (Cost) Electricity gas meter | 1 min | Sum(Energy*Price) per utility | Yes | Yes | Yes
1107 | Building | : HVAC Energy use | Total HVAC EUI | kWh/m2/Year | Electricity (kWh); Gas Total (kWh); Area Conditioned (m2) | 1 min | Total AHU Energy/Area | Yes | Yes | No
1108 | Building | : Occupant Satisfaction | Number of Compaints | Number of Compaints | Complaints | Daily | Sum Zone Occupant Complaints | Yes | No | No
Electricty
M1201 | Building | : Electricity Use | Tolal Electrical Consumption | kWh | Utility Meter (kWh) | 1 min | Sum Elec Consumption | Yes | Yes | No
M1202 | Building | : peak power required | Whole Building Peak Power | kWh | Utilty Meter (kW) | 1 min | Determine max value from set | Yes | Yes | No
M1203 | Building | : Normalised Electricty Consumption | Electricty Consumption | kWh/Time Period | Utilty Meter (kWh) | 1 min | None Needed | Yes | Yes | No
M1204 | Building | : Electrical EUI | Electrical EUI | kWh/M2/Year | Utility Meter (kWh); Building Area | 1 min | kWh/ Building net area | Yes | Yes | No
M1205 | Building | : Electrical Cost | Electrical Cost | (Unit of Local Currency | Electicity Utility bill (Cost) | 1 min | Bill or sum(kWh*Rate) | Yes | Yes | Yes
M1206 | Building | : Electricity use | Average Daily Electrical Power | kWh | Electricity (kWh) | 1 min | Sum Daily values/no of values | Yes | Yes | No
1207 | Building | : Electrical CO2 emissions | Electricty Related CO2 Emissions | kgC02/kWh | Electricity Bills (kWh) | Monthly | Net Electricty (kWh)*Electrical CO2 Factor | Yes | Yes | Yes
1208 | Building | : HVAC peak power | Total HVAC Electric Power | kW | HVAC Electricity Sub meter (kWh) | 1 min | sum hvac elec consumption | Yes | Yes | No
1209 | Building | : HVAC Elec Energy Use | Whole Building HVAC Electrical EUI | kWh/m2 | HVAC Electricity Sub meter (kWh) | 1 min | sum HVAC Elec/ Building Area | Yes | Yes | No
Gas
M1301 | Building | : Gas Consumption | Total Gas Use | kWh | Gas Meter or Utility Bill (m3); Builing schedule (hours) | 1 min | Total gas flow | Yes | Yes | No
1302 | Building | : Peak Gas Load | Building Peak Gas Load | kWh | Gas Meter(m3); Building schedule (Hours) | 1 min | Determine Max value from set | Yes | Yes | No
1303 | Building | : Gas Energy Use | Normalised Gas Consumption | kWh/Time Period | Gas Meter(m3) or Utilty Bill;schedule (Hours) | 1 min | None Needed | Yes | Yes | No
M1304 | Building | : Gas energy use intensity | Gas EUI | kWh/m2 | Gas Meter(m3) or Utilty Bill;schedule (Hours) | Yearly | Gas Consumption/Buidling Area | Yes | Yes | No
M1305 | Building | : Gas Cost | Gas Cost | Unit of Local Currency | Gas Meter(m3) or Utilty Bill;schedule (Hours) | Monthly | None Needed | Yes | Yes | Yes
M1306 | Building | : HVAC Gas Energy Use Intensity | HVAC Gas EUI | kWh/m2 | Sum of HVAC Gas Meters | 1 min | HVAC Gas/Area Served | Yes | Yes | Yes
M1307 | Building | : Gas HVAC Consumption | Total HVAC heater Gas Flow | kWh | Sum Heater Gas Meters;schedule | 1 min | Sum Gas Heater Consumption | Yes | Yes | No
1308 | Building | : Daily Gas Consumption | Daily Total Gas flow | kWh | Gas Meter(m3) | Daily | Daily Sum | Yes | Yes | No
1309 | Building | : Gas related CO2 emissions | Gas related CO2 emissions | Tons CO2 | Utility Bill (Conversion Factor);Gas Meter(m3) | 1 min | Gas (kWh)*Gas Convertion Factor | Yes | Yes | Yes
Oil
1401 | Building | : Oil Consumption | Total Oil Use | kWh | Oil Meter (m3) or Utilty Bill | 1 min | Total Oil flow | Yes | Yes | No
1402 | Building | : Peak oil use | Building Peak Oil | kWh | Oil Meter (m3) or Utilty Bill | 10 mins | Determine Max value from set | Yes | Yes | No
1403 | Building | : oil Consumption | Normalised Oil Consumption | kWh/Time Period | Oil Meter (m3) or Utilty Bill | 1 min | None Needed | Yes | Yes | No
1404 | Building | : oil EUI | Oil EUI | kWh/m2 | Oil Meter (m3) or Utilty Bill | Yearly | Oil Consumption/Buidling Area | Yes | Yes | No
1405 | Building | : oil Cost | Oil Cost | Unit of Local Currency | Utility Bill | Monthly | None Needed | Yes | Yes | Yes
1406 | Building | : HVAC oil Consumption | HVAC Oil EUI | kWh/m2 | Sum of HVAC Oil Meters (m3) | 1 min | HVAC Oil/Building Area | Yes | Yes | Yes
1407 | Building | : Daily Oil Consumption | Daily Total Oil Use | kWh | Oil meter (m3) | Daily | Daily Sum | Yes | Yes | No
1408 | Building | : Oil related CO2 emissions | Oil related CO2 emissions | kgC02/kWh | Oil Meter or Utilty Bill (m3) | 1 min | Oil (kWh)*Oil Conversion Factor | Yes | Yes | yes
Water
1501 | Building | : Peak Water Consumption | Building Peak Water | m3 | Water meter (m3) | 1 min | None Needed | Yes | Yes | No
M1502 | Building | : water consumption | Normalised Water Consumption | m3 | Water Meter (m3) OR Utiltiy Bill | 1 min | None Needed | Yes | Yes | No
1503 | Building | : water Use Intensity | Water Use Intensity | m3/m2 | Utiltiy Bill (m3); Building area (m2) | Yearly | Volume Water/Building Area | Yes | Yes | No
M1504 | Building | : Water Cost | Water Cost | Water Cost | Utiltiy Bill (m3); Building area (m2) | Monthly | None Needed | Yes | Yes | Yes
Cooling
M2001 | Building | : Peak Elec Cooling Load | Peak Elec Cooling Load | kW | Sum Electrical Sub Meters Chillers (kWh) | 1 min | None Needed | Yes | Yes | No
M2002 | Building | : Elec Cooling Load | Normalised Elec Cooling Load | kWh/time period | Sum Electrical Sub Meters Chillers (kWh); Schedule (Hours) | 1 min | None Needed | Yes | Yes | No
M2003 | Building | : Chilled Water Output | Generated Cooling | kWh | Chillers Supply Temperature (oC); Chillers Return Temperature (oC);Chillers Flow Rate (m3/s) | 1 min | M*Cpma*DeltaT/Area | Yes | Yes | No
M2004 | Building | : Chilled Plant Efficiency | All Chillers Efficiency | % | Chillers Supply Temperature (oC); Chillers Return Temperature (oC);Chillers Flow Rate (m3/s); Chillers Electricity (kWh) | 1 min | (kW chilled water)/kW elec input | Yes | Yes | No
2005 | Building | : Cooling Load EUI | - Cooling EUI | kWh/m2/Year | Chiller Electricity Sub Meter (kWh) | 1 min | Cooling Elec/Area | Yes | Yes | No
2006 | Building | : Cooling Load EUI | - Cooling EUI | kWh/m3/Year | Chiller Electricity Sub Meter (kWh) | 2 minute | Cooling Elec/Area | Yes | Yes | No
2007 | Building | : Chilled Water Delta T | Chilled Water Loop Delta T | oC | Chillers Supply;Return Temperature (oC); flow rate (m3/s) | 1 min | Supply - Return Temp | Yes | Yes | No
2008 | Building | : Average Chilled Water Supply Temp | Average Daily Chilled water Supply Temperature | oC | Chillers Chilled Water Supply Temperature (oC) | 1 min | Sum Temps/# Readings | Yes | Yes | No
2009 | Building | : Daily Chilled Plant Elec | Daily Chilled Water Plant Electric usage | kWh | Sum Chilled Plant Electricity;chiller; pumps ;cooling tower (kWh) | 1 min | None Needed | Yes | Yes | No
2010 | Building | : Chilled Plant Daily Output | Daily Chilled Water Plant Output | kWh | Supply Temperature (oC); Return Temperature (oC); flow rate (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
2011 | Building | : Time of Max Chilled Water Output | Maximum Time period chilled water output | Minutes | Supply Temperature (oC); Return Temperature (oC); flow rate (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
M2012 | Building | : Daily Chilled Efficiency | Average Daily Chilled water efficiency | % | Supply Temperature (oC); Return Temperature (oC); flow rate (m3/s) | 1 min | M*Cpma*DeltaT/Elec input | Yes | Yes | No
2013 | Building | : Cold Storage Energy Used | Cold Storage Energy Transfer | kWh | Supply Temperature (oC); Return Temperature (oC); flow rate (m3/s) | 1 min | M*Cpma*DeltaT/Elec input | Yes | Yes | No
M2014 | Building | : Chilled plant Rejected Heat | Total Chilled Water Plant Heat Rejection | kWh | Supply Temperature (oC); Return Temperature (oC); flow rate (m3/s) | 1 min | M*Cpma*DeltaT/Elec input | Yes | Yes | No
Heating
M2101 | Building | : Heating Load (Supply + Demand) | Heating Load | kWh + m3 | Sum Gas (Boilers) (m3); Supply Temperaure (oC); Return Temperature (oC); flow rate(m3/s) | 1 min | M*Cpma*DeltaT + (Gas*Calorific Value) | Yes | Yes | No
M2102 | Building | : Peak Heating Load | Peak Heating Load | kWh + m3 | Sum Gas (Boilers) (M3);Supply;Ret Temperature (oC);flow rate(m3/s) | 1 min | M*Cpma*DeltaT + (Gas*Calorific Value) | Yes | Yes | No
M2103 | Building | : Heating Plant Efficiency | Boilers Efficiency | % | Sum Gas (Boilers) (M3);Supply Temperature (oC); Return Temperature (oC);flow rate(m3/s) | 1 min | SuM*Cpma*DeltaT/Egas) | Yes | Yes | No
2104 | Building | : Heating Load EUI (Area) | - Heating EUI | kWh/m2Area Heated/Year | Supply Temperature (oC); Return Temperature (oC);flow rate(m3/s); Area Heated (m2) | 1 min | SuM*Cpma*DeltaT)/Area | Yes | Yes | No
2105 | Building | : Heating Load EUI (Vol) | - Heating EUI | (kWh/m3Volume Heated/Year | Supply Temperature (oC); Return Temperature (oC);flow rate(m3/s); Area Heated (m2) | 1 min | SuM*Cpma*DeltaT)/Area | Yes | Yes | No
M2106 | Building | : Daily Heating Energy Use | Daily Total Heating Energy Use | kWh | Supply Temperature (oC); Return Temperature (oC);flow rate(m3/s) | 1 min | SuM*Cpma*DeltaT) | Yes | Yes | No
Lighting
2201 | Building | : Lighting Efficiency | Lighting Efficiency | Lux/Watt | Lighing Sensor (Lux); Lighting Circuit Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
2202 | Building | : Lighting EUI | Lighting EUI | kWh/m2/Year | Lighting Ciricut Electricity (kWh) | 1 min | Watts (Lighting)/Lit floor area | Yes | Yes | No
M2203 | Building | : Lighting Energy Use | Lighting Energy Use | kWh | Lighting Ciricut Electricity (kWh); Occupancy (CO2 ) | 1 min | None Needed | Yes | Yes | No
2204 | Building | : Luminous Efficacy | Luminous Efficacy | Lux/Watt | Zones Lux Levels (Lux); Zone Lighting Electricitys (kWh) | 1 min | Sum Zone Artificial Lux/Zone lighting Electricity | Yes | Yes | No
Ventilation
M2301 | Building | : Air Flow | Total AHUs Air Flow | (m3 | AHU Air Flow Rate (m3)); Duct Static Pressure (Pa) | 1 min | Sum(AHU's Air Flow) | Yes | Yes | No
M2302 | Building | : Total AHUs Specific Power | Total AHU's Specific Power | (kW | AHU Supply Fan Electricity (kWh) ; Return Fan Electricity (kWh) | 1 min | Sum(Supply + Return Elec) | Yes | Yes | No
2303 | Building | : Ventilation Efficiency | Ventilation Efficiency | % | AHU Air flow rate(M3); AHU inlet pressure (Pa); AHU outlet pressure(Pa) | 1 min | Sum(Fan Power Delivered )/Sum(ElecIn) | Yes | Yes | No
M2304 | Building | : OA Temperature Fraction | Outside air temperature fraction | Decimal | Mixed Air Temperature(oC) ; Outside Air Temperature(oC); Return Air Temperature(oC) ; Zone Temperature(oC) | 1 min | (OA-MA)/(RetA -MA) | Yes | Yes | No
M2305 | Building | : OA Damper Fraction | OA Damper Fraction | Decimal | Outside Air Damper Position (%); Return Air Damper Position (%) | 1 min | (OA % Open)/(OA+FA % Open) | Yes | Yes | No
M2306 | Building | : OA Enthalpy Fraction | Outside Air Enthalpy Fraction | Decimal | Mixed Air Temperature(oC); Outside Air Temperature(oC); Ret Air Temperature(oC) ; Zone Temperature (oC); Mixed Air Temperature (oC); Outside Air Temperature (oC); Return Air Humidity (%) | 1 min | h = ha + x hw | Yes | Yes | No
Plug Loads
M2401 | Building | : Plug Load Electricity Use | Electricity Use | kWh | Equipment Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
2402 | Building | : Equipment Peak Load | Equipment Peak Load | kWh | Equipment Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
2403 | Building | : Equipment EUI | Plug Loads EUI | kWh/m2 | Plug Load Electricity (kWh) | 1 min | Elec/Area | Yes | Yes | No
People Movers
M2501 | Building | : People Mover Elec | People Mover Energy Use | kWh | People Mover Electricity (kWh) | 1 min | Sum(Elec People Movers) | Yes | Yes | No
Pumping
2601 | Building | : Pumping Electrical Consumption | Pumping Electrical Consumption | kWh | Pumps Electricity consumption (kWh) | 1 min | Sum Pumps Elec | Yes | Yes | No
Hot Water
2701 | Building | : Hot Water Consumption | Hot Water Consumption | kWh | Hot Water Consumptions (kWh) | 1 min | Sum Hot Water Energies | Yes | Yes | No
Humidification
2801 | Building | : Humidifying Energy Consumption | Humidifying Energy Consumption | kWh | Humidifiers Energy Consumption (kWh) | 1 min | Sum Humidifiers Energies | Yes | Yes | No
1601 | Building Storey | : Storey Elec Consumption | Storey Electrical Consumption | kWh | Storey Electricity Sub Meter (kWh) | 1 min | None Needed | Yes | Yes | No
M1701 | Zone | : Zone Temp | Zone Temperature | oC | Zone Temperature (oC); Occupancy (CO2) | 1 min | None Needed | Yes | Yes | No
M1702 | Zone | : Zone Humidity | Zone Humidity | % | Zone Humididy (%); Occupancy (CO2) | 1 min | None Needed | Yes | Yes | No
M1703 | Zone | : Air Velocity | Zone Air Velocity | m/s | Zone Air Velocity(m/s); Occupancy(CO2) | 1 min | None Needed | Yes | Yes | No
1704 | Zone | : Thermal Comfort Critera | Predicted Mean Vote (PMV) or Percentage of People Dissatisfied (PPD) | PMV or PPD | Zone Temperature (oC); Mean Radiant Temperature(oC); Air Velocity (m/s); Zone Humidity (%); Metabolic rate(w/m2); Clothing Insulation (clo) | 1 min | 4 + (0.303 exp(-0.036H) + 0.0275) x {6.57 + 0.46H + 0.31Pa + 0.0017HPa + 0.0014HTa - 4.13 fcl (1 + 0.01dT) (Tcl - Tr) - hcfcl (Tcl - Ta)} | No | Yes | No
1705 | Zone | : Zone Integrity | Zone Integrity Signal (Windows and Doors Closed??) | Windows and Doors Closed?? | Doors/Windows Closed (Yes/No) | 1 min | None Needed | Yes | Yes | No
1706 | Zone | : Zone Occupancy | Zone Occumpancy Level | No of People | Zone Occupancy (No of People) | 1 min | None Needed | Yes | Yes | No
1707 | Zone | : Zone Occupied Status | Zone Occupancy Level | Zone Occupancy Level | Number of People (People) | 1 min | None Needed | Yes | Yes | No
1708 | Zone | : Zone Lux levels | Zone Lux Levels | Zone Lux Levels | Light Level Measurement (Lux) | 1 min | None Needed | Yes | Yes | No
1709 | Zone | : Daylighting Autonomy | Daylighting Autonomy | % | Indoor Natural Light Levels (Lux); Zone Occupancy Schedule (Hours) | 1 min | Adaquate Natural Light Hours/Occupied Hours | Yes | Yes | No
1710 | Zone | : Zone Occupant Complaints | Zone Occupant Complaints | Zone Occupant Complaints | Occupant Complaints (Integer Value) | 1 Hour | Sum Occupant Complaints | No | No | No
1711 | Zone | : Luminous Efficacy | Luminous Efficacy | Lux/Watt | Zones Lux Levels (Lux); Zone Lighting Electricity (kWh) | 1 min | Lux/kWh | Yes | Yes | No
1712 | Zone | : Task Illumience Installed to Required Ratio | Task Lighting Illumience to Required Ratio | % | Light Level Measurement (Lux); Light Level Requirment (Lux) | 1 min | Measured Lux/Required Lux | Yes | Yes | No
1713 | Zone | : Outward Visibility | Outward Visibility Available | Yes/No | Site Study | Not Applicable | None Needed | No | No | No
1714 | Zone | : Daylighting Glare | Daylighting Glare | >= 24 | See Chauvel et al 1982 | 1 min | See Chauvel et al. 1982 | No | Yes | No
1715 | Zone | : Hourly average Predicted Percentage Dissatisfied (PPD) | Hourly average Predicted Percentage Dissatisfied (PPD) | PPD | v = Air Velocity (m/s); Ta = Air Temperature (oC); Tu = Turbulence Intensity | 1 min | 3.413(34-Ta)(v-0.05)0.622 + 0.369vTu(34-Ta)(v-0.05)0.622 | Yes | Yes | No
1716 | Zone | : Hours % when PPD is in comfort Range (10%) | Hours % when PPD is in comfort Range (10%) |  | v = Air Velocity (m/s); Ta = Air Temperature (oC); Tu = Turbulence Intensity | 1 min | 3.413(34-Ta)(v-0.05)0.622 + 0.369vTu(34-Ta)(v-0.05)0.623 | Yes | Yes | No
1717 | Zone | : Hourly average PPD during office hours over one year | Hourly average PPD during office hours over one year |  | v = Air Velocity (m/s); Ta = Air Temperature (oC); Tu = Turbulence Intensity | 1 min | 3.413(34-Ta)(v-0.05)0.622 + 0.369vTu(34-Ta)(v-0.05)0.624 | Yes | Yes | No
1718 | Zone | : Hours (%) when the PPD is in the comfort range (%) | Hours (%) when the PPD is in the comfort range (%) |  | v = Air Velocity (m/s); Ta = Air Temperature (oC); Tu = Turbulence Intensity | 1 min | 3.413(34-Ta)(v-0.05)0.622 + 0.369vTu(34-Ta)(v-0.05)0.625 | Yes | Yes | No
1719 | Zone | : Average PPD of workers in different activities and clothing levels | Average PPD of workers in different activities and clothing levels |  | v = Air Velocity (m/s); Ta = Air Temperature (oC); Tu = Turbulence Intensity | 1 min | 3.413(34-Ta)(v-0.05)0.622 + 0.369vTu(34-Ta)(v-0.05)0.626 | Yes | Yes | No
1720 | Zone | : Airflow rate vairation in different rooms within a single thermostat zone | Zone Air Flow Rate | m/s | Zone Air Flow Rates (m/s) | 1 min | Compare Zone air flow rates | Yes | Yes | No
SYSTEMS and SYSTEM COMPONENTS
1801 | Naural Ventilation System | : Comfertable Zone Conditions | Zone Thermal Comfort | PMV or PPD | Air Flow Rate (m3/s); Air Velocity (m/s); Dry Bulb Temperature (oC); Humidity (%) | 1 minute | PPD or PMV Calculation | Yes | Yes | No
3001 | Air System | : Air Sys Energy Use | Sys Energy Consumption | kWh | Each Component Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
M3002 | Air System | : AHU Total Power | Air Handler Total Power | kWh | Supply ; Return fan Electricity (kWh) | 1 min | Supply +Return elec | Yes | Yes | No
M3003 | Air System | : AHU Specific Power | AHU Specific Power | kW/m3 | Sum Electricity Power(kWh) Flow Rate (m3) | 1 min | (Sum Elec Power)/(Sum Flow Rate) | Yes | Yes | No
3004 | Air System | : Air Sys EUI | Sys EUI | kWh/m2 | Each Component Electricity (kWh)/Area (m2) | 1 min | Elec/area | Yes | Yes | No
3005 | Air System | : Daily AHU Elec | Daily Total AHU Electrical Usage | kWh | Supply ; Return Fan Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
M3006 | Air System | : Daily Total AHU Volume | Daily Total AHU Volume | m3 | AHU Flow rate(m3); | 1 min | None Needed | Yes | Yes | No
3007 | Air System | : Peak AHU Volume | Daily Maximum AHU Volume | m3 | AHU Flow rate(m3);Zones Temps (oC) | 1 min | None Needed | Yes | Yes | No
M3008 | Air System | : Daily Average AHU Power | Daily average Total AHU System Specific Power | kWh | AHU Flow rate(m3);Supply ; Ret fan power (kW) | 1 min | (Supply + Return Elec)/Time Period | Yes | Yes | No
3009 | Air System | : Air Flow and Outdoor Dry Bulb | Daily Average Outdoor Dry Bulb V Total Air Flow | Daily Average Outdoor Dry Bulb V Total Air Flow | Outside Air Dry Bulb Temperature (oC);Air Flow Volume (M3); Zones Temperatures (oC) | 1 min | None Needed | Yes | Yes | No
M3101 | Fan | : Fan Energy Consumption | Fan Energy Consumption | kWh | Fan Electricity (kWh); Air Flow Rate (m3) | 1 min | None Needed | Yes | Yes | No
M3102 | Fan | : VFD Speed Signal | VFD Fan Signal | Hz | Fan VFD Signal Meter (Hz) | 1 min | None Needed | Yes | Yes | No
3103 | Fan | : Fan Efficiency | Fan Efficiency | % | Fan Electricity (kWh); Air Flow rate (m3); Duct Total Pressure Fan Inlet (Pa); Duct Total Pressure Fan Outlet(Pa) | 1 min | (Sum(V*deltaP)/Elec Energy) | Yes | No | No
3104 | Fan | : Fan Hours of Use | Hours Run | Hours Run | On/Off Status | 1 min | None Needed | Yes | Yes | No
3201 | Fan Coil Unit | : Heating Energy use | Heating Energy Use | kWh | Supply Inlet Temperature (oC); Supply outlet Temperature (oC); Flow Rate (m3); Electricity (kWh) | 1 min | (M*Cpma*DeltaT) + Elec | Yes | Yes | No
3202 | Fan Coil Unit | : Heating Efficiency | Heating Efficiency | % | Supply Inlet Temperature (oC); Supply outlet Temperature (oC); Flow Rate (m3); Electricity (kWh) | 1 min | Air Energy Gain/Total Input | Yes | Yes | No
3203 | Fan Coil Unit | : Cooling Energy Use | Cooling Energy Use | kWh | Supply Inlet Temperature (oC); Supply outlet Temperature (oC); Flow Rate (m3); Electricity (kWh) | 1 min | (M*Cpma*DeltaT) + Elec | Yes | Yes | No
3204 | Fan Coil Unit | : Cooling Efficiency | Cooling Efficiency | % | Water Inlet Temperature (oC); Water Outlet Temperature (oC); Water Flow Rate (l/s); Air Inlet Temperature (oC); Air Outlet Temperature (oC); Air Flow Rate (m3/s); Electricity (kWh) | 1 min | Air Energy Gain/Total Input | Yes | Yes | No
M3301 | Mixing Box | : Temperature Setpoint | Mixing Box Temperature Setpoint | oC | Mixed Air Temperature(oC) | 1 min | h = ha + x hw | Yes | Yes | No
M3302 | Mixing Box | : Humidity Setpoint | Mixing Box Humididty Setpoint | % | Mixed Air Humidity (%) | 1 min | RH = RHa + x RHw | Yes | Yes | No
M3303 | Mixing Box | : Enthalpy Setpoint | Mixing Box Enthalpy Setpoint | kJ/kg | Mixed Air Temperature(oC) | 1 min | T= Ta + x Tw | Yes | Yes | No
3302 | Mixing Box | : Mixing Box Damper Position | Mixing Box Damper Position | % | Damper position sensor (%); Mixed Air Temp (oC) | 1 min | None Needed | Yes | Yes | No
3401 | Air to Air Heat Rec | : Energy Transfer | Air To Air HR Energy Transfer Rate | kW | Supply inlet Temperature (oC); Supply outlet Temperature (oC); Flow rate (m3/s); Return inlet Temperature (oC); Return outlet Temperature (oC); Flow rate (m3/s) | 1 min | in separate sheet | Yes | Yes | No
M3402 | Air to Air Heat Rec | : Efficiency | Air to Air HR Efficiency | % | Supply inlet Temperature (oC); Supply outlet Temperature (oC); Flow rate (m3/s); Return inlet Temperature (oC); Return outlet Temperature (oC); Flow rate (m3/s) | 1 min | in separate sheet | Yes | Yes | No
[8 empty] | Yes | Yes | No
3501 | Wheel | : Energy Transfer | Air To Air HR Energy Transfer Rate | kW | Supply Flow Rate (m3/s); Supply Air Humidity Ratio (kg/kg); Return Flow Rate (m3/s); Return Air Humidity Ratio (kg/kg) | 1 min | Ws(*2-*1) ASHRAE Sys 44.4 | Yes | Yes | No
M3502 | Wheel | : Efficiency | Air to Air HR Efficiency | % | Supply Flow Rate (m3/s); Supply Air Humidity Ratio (kg/kg); Return Flow Rate (m3/s); Return Air Humidity Ratio (kg/kg) | 1 min | Ws(*2-*1)/Wmin(*3-*1) | Yes | Yes | No
3601 | Heat Pipe | : Heat Pipe Efficiency(Sensible Only) | Heat Pipe Efficiency | % | Supply inlet Temperature (oC); Supply outlet Temperature (oC); Flow rate (m3/s); Return inlet Temperature (oC); Return outlet Temperature (oC); Flow rate (m3/s) | 1 min | Ws(TSout-TSin)/Wmin(TSRETin-*Sin) | No | Yes | No
3701 | Humidifier | : Humidificaion Load | Humididfication Load | kg/hour | Air Flow Rate (m3/s); Indoor Dry Bulb Temperature (oC); Outdoor Dry Bulb Temperature (oC); Indoor Relative Humidity (%); Indoor Relative Humidity (%) | 1 min | 3.6pQo(Wi-Wo)-S+L | Yes | Yes | No
3801 | Dehumidifier | : Performance Efficicency | Humidifier Efficicency | % | Inlet Wet Bulb Temperature (oC) ; Dry Bulb Temperature Inlet (oC); Wet Bulb Outlet Temperature (oC); Dry Bulb Outlet Temperature (oC) | 1 min | (hin-hout)/(hin-hWet Bulbout(100%)) | Yes | Yes | No
3901 | Terminal Box | : Supply Temperature | Supply Air Temperature | oC | Temperature (oC) | 1 min | None Needed | Yes | Yes | No
3902 | Terminal Box | : Supply Air Velocity | Supply Air Velocity | m3 | Air Velocity (M/S) | 1 min | None Needed | Yes | Yes | No
3903 | Terminal Box | : Air Flow Rate | Supply Air Flow Rate | m/s | Air Flow Rate (M3/S) | 1 min | None Needed | Yes | Yes | No
3904 | Terminal Box | : Pressure | Duct Pressure | Pa | Duct Air Pressure (Pa) | 1 min | None Needed | Yes | Yes | No
3905 | Terminal Box | : Humidity | Supply Air Relative Humidity | % | Humidity (%) | 1 min | None Needed | Yes | Yes | No
3911 | Dual Duct Box | : Supply Temperature | Supply Air Temperature | oC | Zone Temperature (oC); Supply Temperature (oC); Hot Damper(%); Cold Damper(%); Flow(m3/s); Supply Temperature (oC) | 1 min | None Needed | Yes | Yes | No
3912 | Dual Duct Box | : Supply Air Flow Rate | Supply Volumetric Flow Rate | m3/s | Zone Temperature (oC); Supply Temperature (oC); Hot Damper(%); Cold Damper(%); Flow(m3/s); Supply Temperature (oC) | 1 min | None Needed | Yes | Yes | No
3913 | Dual Duct Box | : Supply Air Humdidty | Supply Air Humidity | % | Zone Temperature (oC); Supply Temperature (oC); Hot Damper(%); Cold Damper(%); Flow(m3/s); Supply Temperature (oC) | 1 min | none Needed | Yes | Yes | No
3920 | FumeHood | : Elec Consumption | Elec Use | kWh | kW | 1 min | None Needed | Yes | Yes | No
3921 | FumeHood | : Hours of Use | Hours of Use | Hours | On/Off Status; Experiment in Progress | 1 min | None Needed | Yes | Yes | No
| Heating Coil | Refer to Object at Tag 6101 | [5 empty] | Yes | Yes | No
| Cooling Coil | Refer to Object at Tag 4401 | [5 empty] | Yes | Yes | No
| Compressed Air | : Effectiveness | kWh per Nominal meters cubed | kWh/Nm3 | Electricity (kWh); m3 air output (m3) | 1 min | kWh/m3 | Yes | No | No
M4001 | Cooling System | : Chiled Plant Power | Total Chillers Power | kW | Chillers Electricity (kWh) | 1 min | Sum Chillers Elec | Yes | Yes | No
M4002 | Cooling System | : Chilled Plant Output | Total Chillers Output | kWh | Supply inlet Temperature (oC); Supply outlet Temperature (oC); Supply flow rate (m3/s) | 1 min | SuM*Cpma*DeltaT) | Yes | Yes | No
4003 | Cooling System | : Chilled Plant Heat of Rejection | Total Chilled Water Plant Heat of Rejection | kWh | Sum Condenser Loops Load | 1 min | Sum(Condenser Loops) | Yes | Yes | No
M4004 | Cooling System | : Chill Water Plant Heat Balance | Chilled Water Plant Heat Balance | kWh | Supply inlet Temperature (oC); Supply outlet Temperature (oC); Supply flow rate (m3/s) | 1 min | SuM*Cpma*DeltaT) | Yes | Yes | No
M4101 | Chiller | : Chiller Energy Use | Chiller Energy Use | kW | Electricity (kWh) | 1 min | none needed | Yes | Yes | No
M4102 | Chiller | : Chiller COP | COP | Decimal Value | Inlet Temperature (oC); Outlet Temperature (oC); Coolant Circuit Flow rate (l/s); Electricity (kWh) | 1 min | (M*Cpma*DeltaT)/Elec Meter | Yes | Yes | No
4103 | Chiller | : Chiller Load V Outdoor Dry Bulb | Daily Average Outdoor Dry Bulb V Daily Chiller Load | oC V kWh | Electricity (kWh); Outdoor Dry Bulb (oC) | 1 min | None Needed | Yes | Yes | No
M4104 | Chiller | : Chiller Hours of Use | Hours of Use | Hours | On/Off Status (%) | 1 min | None Needed | Yes | Yes | No
M4201 | Cooling Tower | : Cooling Tower Heat Rejected | Cooling Tower Heat Loss | (kWh | Refrigerant Supply Temperature (oC); Return Temperature (oC); Flow Rate (l/s) | 1 min | SuM*Cpma*DeltaT) | Yes | Yes | No
[8 empty] | Yes | Yes | Yes
Thermal Storage |  |  | 3501 | 3501 |  |  |  | Yes | Yes | Yes
[8 empty] | Yes | Yes | Yes
| Humidifier | same as above | [5 empty] | Yes | Yes | Yes
[8 empty] | Yes | Yes | Yes
| Evaporative Cooler |  | Chiller Energy Use (kW) | Chiller Energy Use (kW) | Electricity | 1 min | none needed | Yes | Yes | Yes
|  |  | Chiller Efficiency (%) | Chiller Efficiency (%) | Inlet;outlet Temperature; Flow rate (demand) | 1 min | M*Cp*deltaT/elec input | Yes | Yes | Yes
|  |  | COP (Decimal Value) | COP (Decimal Value) |  | 1 min | None Needed | Yes | Yes | Yes
3301 |  |  | Daily Average Outdoor Dry Bulb V Daily Chiller Load | Daily Average Outdoor Dry Bulb V Daily Chiller Load |  | 1 min | None Needed | Yes | Yes | Yes
3302 | [7 empty] | Yes | Yes | Yes
4301 | Condenser | : Condenser Loop Load | Plant Condenser Loop Thermal Load | (kWh | Refrigerant Supply Temperature (oC); Return Temperature (oC); Flow Rate (l/s) | 1 min | SuM*Cpma*DeltaT) | Yes | Yes | No
| Pump | Refer to Object at Tag 6201
[8 empty] | Yes | Yes | No
4401 | Cooling Coil | : Required Energy Transfer Rate | Cooling Coil Energy Use | kWh | Air Inlet Temperature (oC); Air Outlet Temperature (oC); Water Inlet Temperature (oC); Water Outlet Temperature (oC); Air Flow Rate (m3/s); Water Flow Rate(m3); Valve Status (%) | 1 min | M*Cpma*DeltaTm | Yes | Yes | No
M4402 | Cooling Coil | : Efficiency | Cooling Coil Efficiency | % | Air Inlet Temperature (oC); Air Outlet Temperature (oC); Water Inlet Temperature (oC); Water Outlet Temperature (oC); Air Flow Rate (m3/s); Water Flow Rate(m3); Valve Status (%) | 1 min | Air energy in/water energy out | Yes | Yes | No
4501 | Thermal Storage | : Cold Storage Transfer In | Cold Storage Energy Transfer | kWh | Supply ; flow rate (Water) IN (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
4502 | Thermal Storage | : Cold Storage Use (OUt) | Cold Storage Energy use | kWh | Supply Temperature; Flow Rate Water OUT(m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
M4503 | Thermal Storage | : Cold Storage Efficiency | Cold Storage Efficiency | % | Supply Temperature (oC); Flow rate (Water) (m3/s) | 1 min | (Energy Out)/(Energy In) | Yes | Yes | No
M4601 | Chilled Beam | : Energy Consumption | Energy Consumption | kWh | Supply inlet temperature (oC); Supply outlet temperature (oC); Mean Radiant Temperature (oC); Flow rate (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
M4701 | Direct Evap Cool | : Saturation Effectiveness | Saturation Effectiveness | % | Supply Inlet Dry Bulb Temperature (oC); Supply Outlet Wet Bulb Temperature (oC); Inlet Wet Bulb Temperature (oC) | 1 min | 100(Dry Bulbin- Dry Bulbout)/(Dry Bulbin-Wet Bulbin) | Yes | Yes | No
M4801 | Indirect Evap Cool | : Saturation Effectiveness | Saturation Effectiveness | % | Supply Side Inlet Temperature (oC); Supply Side Outlet Temperature (oC); Return Inlet Wet Bulb Temperature (oC) | 1 min | 100(SDry Bulbin- SDry Bulbout)/(SDry Bulbin-RetWet Bulbin) | Yes | Yes | No
M4901 | Roof Spray System | : System Efficiency | Roof Spray System Efficiency | % | Pump (Elec); Water Supply Temperature (oC); Return Temperature (oC) ; Flow Rate (m3) | 1 min | Chilled Water Use/Pump Elec | Yes | No | No
M4902 | Roof Spray System | : Energy Use | Pump Electricity Use | kWh | Pump Electricity (kWh) | 1 min | None Needed | Yes | No | No
M4903 | Roof Spray System | : Make Up Water | Volume of Make up Water | m3 | Water Volume (m3) | 1 min | None Needed | Yes | No | No
4911 | Purchased Cooling | : Purchased Heating Energy | Purchased Heating Energy | kWh | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | (M*Cpma*DeltaT) | Yes | Yes | No
4912 | Purchased Cooling | : Purchased Heating Cost | Purchased Heating Cost | Local Currency | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s); Utiltiy Tarrif | 1 min | (M*Cpma*DeltaT)*Tarrif | Yes | Yes | Yes
M5001 | Heating System | : Heating System Output | Total Boilers Output | kWh | Boilers Flow rate (l/s); Inlet Temperature (oC); Outlet Temperature (oC) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
M5001 | Heating System | : Heating Fuel Consumption | Total Boilers Gas Flow | m3 | Boilers Gas Meters (m3) | 1 min | None Needed | Yes | Yes | No
M5101 | Boiler | : Boiler Efficiency | Boiler Efficiency, | % | Boiler Gas (m3) | 1 min | Boiler Output/M3*Constant | Yes | Yes | No
5102 | Boiler | : Boiler Energy Output | Boiler Energy Output | kWh | Flow rate (m3/s);Inlet Outlet Temperature (oC) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
5103 | Boiler | : Boiiler Gas Flow | Total Boiler Gas Flow | m3 | Boiler Gas Meter (m3) | 1 min | None Needed | Yes | Yes | No
5104 | Boiler | : Boiler Gas V Outdoor Dry Bulb | Daily Average Outdoor Dry Bulb V Daily Boiler Load | oC V kWh | Outdoor Dry Bulb (oC) | 1 min | None Needed | Yes | Yes | No
5105 | Boiler | : Daily Gas Consumption | Maximum Daily Total Boiler Heating Energy | kWh | Flow rate (m3/s); Inlet Outlet Temperature (oC) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
5106 | Boiler | : Boiler Hours of Use | Hours of Use | Hours | On/Off Status (%) | 15 Minutes | None Needed | Yes | Yes | No
M5201 | Solar Photovoltaic | : Total PV Production | Total PV System Production | kWh/Time Period | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5202 | Solar Photovoltaic | : PV StanDry Bulby Production | PV System StanDry Bulby Use | kWh/Time Period | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5203 | Solar Photovoltaic | : Net PV Production | Net PV System Production | kWh/Time Period | Electricity (kWh) | 1 min | Total - StanDry Bulby | Yes | Yes | No
5204 | Solar Photovoltaic | : Equivalent Hours PV Prod | Equivalent Hours Peak PV Production | hrs/day/kWp | Electricity (kWh) | 1 min | Net PV Energy/Rated Capacity | Yes | Yes | No
5205 | Solar Photovoltaic | : Equivalent Annual Hours | Equivalent Annual Hours Peak PV Product | hrs/yr/kWp | Electricity (kWh) | 1 min | Net PV Energy/Rated Capacity | Yes | Yes | No
5206 | Solar Photovoltaic | : Offset Facility Elec Load | Facility Electrical Load Offset by PV Production | % | Photo Voltaic (kWh); Main Electricity (kWh) | 1 min | PV Elec/Net Building Elec | Yes | Yes | No
5207 | Solar Photovoltaic | : Offset Facility Total Load | Facility Total Energy Load Met by PV Production | % | Photo Voltaic (kWh) ; Main Electricity(kWh); Gas (M3) | 1 min | PV Energy/Total Energy | Yes | Yes | No
5208 | Solar Photovoltaic | : Total Elec Exported | Total Electricity Exported to Utility | kWh | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5209 | Solar Photovoltaic | : Total Incident Solar | Total Incident Solar Radiation | kWh | Solar Radiation (kWh) | 1 min | None Needed | Yes | Yes | No
5210 | Solar Photovoltaic | : PV Effectiveness | PV System AC Electricity Generation Effectiveness | % | Electricity (kWh); Solar Radiation (kWh) | 1 min | Net PV /Total Solar | Yes | Yes | No
5211 | Solar Photovoltaic | : PV Performance Ratio | PV System Performance Ratio | % | Rated Efficiency (%); Electricity Gen Effectiveness (%) | 1 min | Efficiency/Rated Efficiency | Yes | Yes | No
5212 | Solar Photovoltaic | : Net Facility Energy Use | Net Facility Electricity Use | kWh/Time | Electricity (kWh);Utlilty Bill (Cost) | 1 min | Building Elec Demand - Net PV | Yes | Yes | No
5213 | Solar Photovoltaic | : Peak Elec Demand | Peak Demand of Net Facility Electricity Use | kW/Time | Utility Bill (Cost); Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5214 | Solar Photovoltaic | : Total Peak Demand | Peak Demand of Total Facility Elec Use without PV | kW | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5215 | Solar Photovoltaic | : Peak Demand Reduction | Reduction of Peak Demand because of PV system | kW | Total Electricity (kWh); PV Electricity (kWh) | 1 min | Peak(Total -PV Elec) | Yes | Yes | No
5216 | Solar Photovoltaic | : Elec Costs | Facility Electricity Costs without PV System | Currency | Total Electricity(kWh);Utility Bill (Cost) | 1 min | Kwh * Utility Rate Structure | Yes | Yes | No
5217 | Solar Photovoltaic | : PV Energy Cost Savings | Energy Cost Savings Resulting from PV System | (Currency | PV Electricity;Utilty Bill (kWh) | 1 min | Kwh * Utility Rate Structure | Yes | Yes | No
5218 | Solar Photovoltaic | : Average PV Production | Maximum Time-Series Net PV Production | (kWh/Time | PV Electricity (kWh) | Monthly | Monthly Average | Yes | Yes | No
5219 | Solar Photovoltaic | : Daily Average PV Product | Average Daily Time-Series PV Production | (kWh V time | PV Electricity(kWh) | Daily | Daily Average | Yes | Yes | No
5301 | Solar Water Heater | : Solar Water Heating | Solar Water Heating Delivered | (kWh | Supply Temperature (oC); Return Temperature (oC); Flow Rate (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
5302 | Solar Water Heater | : Solar Water Efficiency | Solar Water Heating Efficiency | % | Solar Radiation (W/m2); Supply Temperature (oC); Return Temperature (oC); Flow Rate (m3/s) | 1 min | Heat Generated/Incident Solar | Yes | Yes | No
5303 | Solar Water Heater | : Solar % of Total Heating | Percentage of Total Heating | % | Inlet Temperature (oC); Outlet Temperature (oC);Flow Rate (m3); Utility Bill (Cost) | 1 min | Solar Water Heated/Total Heat | Yes | Yes | No
5304 | Solar Water Heater | : Savings | Resultant Energy Savings | Unit of Local Currency | Solar Generated (kWh); Total Heating Load (kWh) | Monthly | % Saving*Heating Bill | Yes | Yes | No
5401 | Furnace | : Furnace Efficiency | Furnace Efficiency | % | Fuel Meter (m3); Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | Furnace Output/Fuel consumed | Yes | Yes | No
5402 | Furnace | : Furnace Energy Use | Furnace Energy Output | kWh | Fuel Consumption(m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
5403 | Furnace | : Furnace Gas Flow | Total Furnace Gas Flow | m3 | Fuel Consumption (m3/s) | 1 min | None Needed | Yes | Yes | No
5404 | Furnace | : Furnace Gas V Outdoor Dry Bulb | Daily Average Outdoor Dry Bulb V Daily Furnace Load | oC V kWh | Outdoor Dry Bulb Temperature (oC) | 1 min | None Needed | Yes | Yes | No
5405 | Furnace | : Daily Gas Consumption | Maximum Daily Total Furnace Heating Energy | kWh | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | None Needed | Yes | Yes | No
5601 | CHP | : CHP Efficiency | CHP Total Efficiency | % | Electricity (kWh); Fuel Meter (m3); Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | ηO =(ElecE + Σ QTH)/QFUEL | Yes | Yes | No
5602 | CHP | : Elec Production | CHP Elec Production | kWh | Fuel Meter (m3/s);Electricity Output (kWh) | 1 min | None Needed | Yes | Yes | No
5603 | CHP | : Elec Production Efficiency | CHP Elec Efficiency | % | Fuel Meter (m3/s); Electricity Output (kWh) | 1 min | (Elec Output)/(Fuel In) | Yes | Yes | No
5604 | CHP | : Heat Production | CHP Heat Production | kWh | Fuel Meter (m3); Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
5605 | CHP | : Heat Production Efficiency | CHP Heat Efficiency | % | Fuel Meter (m3); Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | (Heat Output)/(Fuel In) | Yes | Yes | No
5701 | Heat Pump | : Opearation History | Time | % | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
5702 | Heat Pump | : COP | COP | Decimal Value | Electricity (kWh); Evaporator Circuit Supply Temperature (oC); Evaporator Circuit Return Temperature (oC); Evaporator Circuit Flow Rate (m3/s) Condenser Supply Temperature (oC);Condenser Return Temperature (oC); Condenser Circuit Flow Rate (m3/s) | 1 min | ((M*Cpma*DeltaT)out - (M*Cpma*DeltaT)in)/Elec Meter | Yes | Yes | No
5801 | Purchased Heating | : Purchased Heating Energy | Purchased Heating Energy | kWh | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | (M*Cpma*DeltaT) | Yes | Yes | No
5802 | Purchased Heating | : Purchased Heating Cost | Purchased Heating Cost | Local Currency | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s); Utiltiy Tarrif | 1 min | (M*Cpma*DeltaT)*Tarrif | Yes | Yes | Yes
6001 | DHW | : DHW Use | DHW Load | KWh | Supply Temperature (oC);Return Temperature (oC); Flow Rate (m3/s) | 1 min | M*Cp*deltaT | Yes | Yes | No
M6101 | Heating Coil | : Required Energy Transfer Rate | Heating Coil Energy Use | kW | Air In Temperature (oC); Air Out Temperature (oC);Water In Temperature (oC); Water Out Temperature (oC); Air Flow Rate(m3); Water Flow Rate(m3); Valve Status(%) | 1 min | M*Cpma*DeltaTm | Yes | Yes | No
M6102 | Heating Coil | : Efficiency | Heating Coil Efficiency | % | Air In Temperature (oC); Air Out Temperature (oC);Water In Temperature (oC); Water Out Temperature (oC); Air Flow Rate(m3); Water Flow Rate(m3); Valve Status(%) | 1 min | Air energy in/water energy out | Yes | Yes | No
6201 | Pump | : Efficiency | Pump Efficiency | % | Electricity (kWh); Flow meter (l/s); Inlet Pressure (Pa); Outlet Pressure (Pa); Total Pressure (Pa) | 1 min | (V*(deltaP))/(Elec Energy In) | Yes | Yes | No
M6202 | Pump | : Energy Use | Pump Energy Use | kWh | Electricity (kWh) | 1 min | None Needed | Yes | Yes | No
| Pump | : Pump Hours of Use | Hours of Use | Hours | On/Off Status (%) | 1 min | None Needed | Yes | Yes | No
M6301 | Water Storage | : Water Temp | Water Temp | oC | Temperature (oC) | 1 min | None Needed | Yes | Yes | No
M6401 | Under Floor Heating | : Energy Consumption | Energy Consumption | kWh | Inlet Temperature (oC);Outlet Temperature (oC); Mean Radiant Temperature (oC);Flow rate(M3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
M6510 | Radiator Circuit | : Energy Consumption | Energy Consumption | kWh | Inlet Temperature (oC);Outlet Temperature (oC); Flow rate(m3/s) | 1 min | M*Cpma*DeltaT | Yes | Yes | No
People Mover Sys
M7101 | Elevator | : Elevator Electricity | Energy Use | kWh | Elevator Elect (kW); Occupancy (CO2) | 1 min | None Needed | Yes | Yes | No
M7201 | Escalator | : Escalator Electricity | Energy Use | kWh | Escalator Electricity (kW);Occupancy (CO2) | 1 min | None Needed | Yes | Yes | No
M7301 | Walkway | : Walkway Electricity | Energy Use | kWh | Walkway Electricity (kW); Occupancy (CO2) | 1 min | None Needed | Yes | Yes | No

## POQualifierList
Qualifier List which is applicable to all Performance Objectives and Metrics
Minimise
Maximise
Optimise
Reduce
Maintain
Increase
Control
Compare