## ERI_EnergyManagerGeometry
List of Temperature Sensors, CO2 PPM Counters and RH Sensors
Zone Number: Name | Building Object (Zone Number: Name) | Function (Unit) | Required Measurement | Measurement Interval | Comment | Required Tier 1 | Required Tier 2 | Required Tier 3 | Existing Measurement | Exisiting Tier 1 | Existing Tier 2 | Existing Tier 3 | Missing Tier 1 | Missing Tier 2 | Missing Tier 3
West Stairs | West Stairs | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| West Stairs | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| West Stairs | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| West Stairs | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG01:Aquatic tank lab | LG01:Aquatic tank lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG01:Aquatic tank lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG01:Aquatic tank lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG01:Aquatic tank lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG01:Aquatic tank lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG01:Aquatic tank lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LGO2:Aquatic tank holding area | LGO2:Aquatic tank holding area | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LGO2:Aquatic tank holding area | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LGO2:Aquatic tank holding area | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LGO2:Aquatic tank holding area | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LGO2:Aquatic tank holding area | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG03:Water Sys Ctrl Unit | LG03:Water Sys Ctrl Unit | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG03:Water Sys Ctrl Unit | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG03:Water Sys Ctrl Unit | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG03:Water Sys Ctrl Unit | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG03:Water Sys Ctrl Unit | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG04:Sust Energy Lab | LG04:Sust Energy Lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG04:Sust Energy Lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG04:Sust Energy Lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG04:Sust Energy Lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG04:Sust Energy Lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG05:Ecotox incubation | LG05:Ecotox incubation | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG05:Ecotox incubation | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG05:Ecotox incubation | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG05:Ecotox incubation | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG05:Ecotox incubation | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG06:Main Plant Room | LG06:Main Plant Room | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG06:Main Plant Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG06:Main Plant Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG06:Main Plant Room | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG06:Main Plant Room | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG07:Xray Photo | LG07:Xray Photo | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG07:Xray Photo | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG07:Xray Photo | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG07:Xray Photo | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG07:Xray Photo | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG08:Waste Material Storage Area | LG08:Waste Material Storage Area | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG08:Waste Material Storage Area | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG08:Waste Material Storage Area | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG08:Waste Material Storage Area | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG08:Waste Material Storage Area | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG09:Switch Room | LG09:Switch Room | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG09:Switch Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG09:Switch Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG09:Switch Room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG09:Switch Room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG10:ESB Room | LG10:ESB Room | Temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| LG10:ESB Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG10:ESB Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG10:ESB Room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG10:ESB Room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG11:Corridor1.2 | LG11:Corridor1.2 | Temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| LG11:Corridor1.2 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG11:Corridor1.2 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG11:Corridor1.2 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG11:Corridor1.2 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG12:Corridor1.8 | LG12:Corridor1.8 | Temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| LG12:Corridor1.8 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG12:Corridor1.8 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG12:Corridor1.8 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG12:Corridor1.8 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG13:Frozen Storage Area | LG13:Frozen Storage Area | Temp |  | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| LG13:Frozen Storage Area | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG13:Frozen Storage Area | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG13:Frozen Storage Area | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG13:Frozen Storage Area | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG14:ControlledTemp 0 to 15 | LG14:ControlledTemp 0 to 15 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG14:ControlledTemp 0 to 15 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG14:ControlledTemp 0 to 15 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG14:ControlledTemp 0 to 15 | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG14:ControlledTemp 0 to 15 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG15: Controlled Temp 10 to 20 | LG15: Controlled Temp 10 to 20 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG15: Controlled Temp 10 to 20 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG15: Controlled Temp 10 to 20 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG15: Controlled Temp 10 to 20 | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG15: Controlled Temp 10 to 20 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG16:Controlled Temp -15 to 20 | LG16:Controlled Temp -15 to 20 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG16:Controlled Temp -15 to 20 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG16:Controlled Temp -15 to 20 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG16:Controlled Temp -15 to 20 | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG16:Controlled Temp -15 to 20 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG17:Chilled Storage Area | LG17:Chilled Storage Area | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG17:Chilled Storage Area | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG17:Chilled Storage Area | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG17:Chilled Storage Area | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG17:Chilled Storage Area | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG18:Flammables Store | LG18:Flammables Store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG18:Flammables Store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG18:Flammables Store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG18:Flammables Store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG18:Flammables Store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG19:Central Chemical/Poison Store | LG19:Central Chemical/Poison Store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG19:Central Chemical/Poison Store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG19:Central Chemical/Poison Store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG19:Central Chemical/Poison Store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG19:Central Chemical/Poison Store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG20:Hazardous Chemical Store | LG20:Hazardous Chemical Store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG20:Hazardous Chemical Store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG20:Hazardous Chemical Store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG20:Hazardous Chemical Store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG20:Hazardous Chemical Store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG:21Lobby | LG:21Lobby | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG:21Lobby | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG:21Lobby | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG:21Lobby | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG:21Lobby | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG22:Storage | LG22:Storage | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG22:Storage | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG22:Storage | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG22:Storage | Occupancy | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG22:Storage | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG23:Teaching lab | LG23:Teaching lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG23:Teaching lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG23:Teaching lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG23:Teaching lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG23:Teaching lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG23:Teaching lab | Lux Sensor |  | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG24:Eco-seperations lab | LG24:Eco-seperations lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG24:Eco-seperations lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG24:Eco-seperations lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG24:Eco-seperations lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG24:Eco-seperations lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG24:Eco-seperations lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG25:Sedimentology lab | LG25:Sedimentology lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG25:Sedimentology lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG25:Sedimentology lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG25:Sedimentology lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG25:Sedimentology lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG25:Sedimentology lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG26:Microfossils lab | LG26:Microfossils lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG26:Microfossils lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG26:Microfossils lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG26:Microfossils lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG26:Microfossils lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG26:Microfossils lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG27:Ecocotoxology lab | LG27:Ecocotoxology lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG27:Ecocotoxology lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG27:Ecocotoxology lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG27:Ecocotoxology lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG27:Ecocotoxology lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG27:Ecocotoxology lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG28:General Wet prep | LG28:General Wet prep | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG28:General Wet prep | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG28:General Wet prep | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG28:General Wet prep | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG28:General Wet prep | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG28:General Wet prep | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG29:Field samp store | LG29:Field samp store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG29:Field samp store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG29:Field samp store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG29:Field samp store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG29:Field samp store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG29:Field samp store | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG30:Sample reception | LG30:Sample reception | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| LG30:Sample reception | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG30:Sample reception | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| LG30:Sample reception | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG30:Sample reception | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| LG30:Sample reception | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Hall | Hall | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Hall | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Hall | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Hall | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Hall | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Corridor1.14 | Corridor1.14 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Corridor1.14 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Corridor1.14 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Corridor1.14 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Corridor1.14 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
HCWC | HCWC | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| HCWC | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| HCWC | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| HCWC | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| HCWC | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
East Stairs | East Stairs | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| East Stairs | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| East Stairs | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| East Stairs | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
[7 empty] | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G01:Fresh water an lab | G01:Fresh water an lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G01:Fresh water an lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G01:Fresh water an lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G01:Fresh water an lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G01:Fresh water an lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G01:Fresh water an lab | Lux Sensor |  | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G02:Marine Biol an lab | G02:Marine Biol an lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G02:Marine Biol an lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G02:Marine Biol an lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G02:Marine Biol an lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G02:Marine Biol an lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G03:Aqua fish lab | G03:Aqua fish lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G03:Aqua fish lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G03:Aqua fish lab | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G03:Aqua fish lab | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G03:Aqua fish lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G04:genetics | G04:genetics | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G04:genetics | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G04:genetics | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G04:genetics | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G04:genetics | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G05:immunology | G05:immunology | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G05:immunology | Dry Bulb Temperture |  | 1 Minute
| G05:immunology | Dry Bulb Temperture |  | 1 Minute
| G05:immunology | Dry Bulb Temperture |  | 1 Minute
Radiant temp | G05:immunology | Radiant temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Occupancy | G05:immunology | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Relative Humidty | G05:immunology | Relative Humidty | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G05:immunology | Relative Humidty |  | 1 Minute
| G05:immunology | Relative Humidty |  | 1 Minute
| G05:immunology | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G05:immunology | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G05:immunology | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| G05:immunology | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G05:immunology | Lux Sensor | 1 | 1 Minute |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
| G05:immunology | Lux Sensor |  | 1 Minute
| G05:immunology | Lux Sensor |  | 1 Minute
G06:biodiversity | G06:biodiversity | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Biodiversity top surface | Biodiversity top surface | slab temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Biodiversity top embedded | Biodiversity top embedded | slab temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Biodiversity lower embedded | Biodiversity lower embedded | slab temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Biodiversity lower surface | Biodiversity lower surface | slab temp | 1 | 1 Minute |  |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Biodiversity lower surface | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Biodiversity lower surface | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Biodiversity lower surface | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Biodiversity lower surface | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G07:environ info | G07:environ info | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G07:environ info | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G07:environ info | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G07:environ info | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G07:environ info | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G08:general computing | G08:general computing | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G08:general computing | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G08:general computing | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G08:general computing | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G08:general computing | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G09:tech prep | G09:tech prep | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G09:tech prep | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G09:tech prep | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G09:tech prep | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G09:tech prep | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G10GWCM:wc/m | G10GWCM:wc/m | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G10GWCM:wc/m | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G10GWCM:wc/m | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G10GWCM:wc/m | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G10GWCM:wc/m | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G11:GWCF:wc/f | G11:GWCF:wc/f | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G11:GWCF:wc/f | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G11:GWCF:wc/f | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G11:GWCF:wc/f | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G11:GWCF:wc/f | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G12: Toilet Lobby | G12: Toilet Lobby |  |  | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
G13:EntranceLobby | G13:EntranceLobby |  |  | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
G14:photograph archive | G14:photograph archive | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G14:photograph archive | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G14:photograph archive | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G14:photograph archive | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G14:photograph archive | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G15:wet specimen store | G15:wet specimen store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G15:wet specimen store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G15:wet specimen store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G15:wet specimen store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G15:wet specimen store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G16 | G16 |  |  | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
G17:dry specimen store | G17:dry specimen store | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G17:dry specimen store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G17:dry specimen store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G17:dry specimen store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G17:dry specimen store | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G18:tissue culture room | G18:tissue culture room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G18:tissue culture room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G18:tissue culture room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G18:tissue culture room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G18:tissue culture room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G19:comms room | G19:comms room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G19:comms room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G19:comms room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G19:comms room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G19:comms room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G20:hcwc | G20:hcwc | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G20:hcwc | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G20:hcwc | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G20:hcwc | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G20:hcwc | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G:21:Hall2.16 | G:21:Hall2.16 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G:21:Hall2.16 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:21:Hall2.16 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:21:Hall2.16 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G:21:Hall2.16 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G22:open office 2.2 | G22:open office 2.2 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Radiant Temp | G22:open office 2.2 | Radiant Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Occupancy | G22:open office 2.2 | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Relative Humidity | G22:open office 2.2 | Relative Humidity | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G22:open office 2.2 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G22:open office 2.2 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G22:open office 2.2 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G22:open office 2.2 | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G23:Break Out Space 2.6 | G23:Break Out Space 2.6 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G23:Break Out Space 2.6 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G23:Break Out Space 2.6 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G23:Break Out Space 2.6 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G23:Break Out Space 2.6 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G23:Break Out Space 2.6 | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G24:open office 2.10 | G24:open office 2.10 (Same as entrance lobby) | Temp | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| G24:open office 2.10 (Same as entrance lobby) | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G24:open office 2.10 (Same as entrance lobby) | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G24:open office 2.10 (Same as entrance lobby) | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G24:open office 2.10 (Same as entrance lobby) | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G24:open office 2.10 (Same as entrance lobby) | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G25:Break Out Space | G25:Break Out Space | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G25:Break Out Space | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G25:Break Out Space | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G25:Break Out Space | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G25:Break Out Space | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G25:Break Out Space | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G26:Visiting Collegiate | G26:Visiting Collegiate | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G26:Visiting Collegiate | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G26:Visiting Collegiate | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G26:Visiting Collegiate | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G26:Visiting Collegiate | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G26:Visiting Collegiate | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G27:Admin Sec | G27:Admin Sec | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G27:Admin Sec | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G27:Admin Sec | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G27:Admin Sec | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G27:Admin Sec | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G27:Admin Sec | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G28 Section Manager | G28 Section Manager | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G28 Section Manager | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G28 Section Manager | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G28 Section Manager | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G28 Section Manager | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G28 Section Manager | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G29:Break Out Space | G29:Break Out Space | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G29:Break Out Space | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G29:Break Out Space | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G29:Break Out Space | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G29:Break Out Space | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G29:Break Out Space | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G30:meeting room | G30:meeting room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G30:meeting room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G30:meeting room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G30:meeting room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G30:meeting room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G30:meeting room | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G:Corridor 2.4 | G:Corridor 2.4 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G:Corridor 2.4 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:Corridor 2.4 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:Corridor 2.4 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G:Corridor 2.4 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G:Corridor2.9 | G:Corridor2.9 | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| G:Corridor2.9 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:Corridor2.9 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| G:Corridor2.9 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| G:Corridor2.9 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.01:AtmosphericChem | 1.01:AtmosphericChem | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.01:AtmosphericChem | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.01:AtmosphericChem | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.01:AtmosphericChem | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.01:AtmosphericChem | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.01:AtmosphericChem | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.02:chem prep | 1.02:chem prep | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.02:chem prep | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.02:chem prep | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.02:chem prep | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.02:chem prep | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.02:chem prep | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.03:supercrit fluids | 1.03:supercrit fluids | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.03:supercrit fluids | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.03:supercrit fluids | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.03:supercrit fluids | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.03:supercrit fluids | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.03:supercrit fluids | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.04:analytical chem | 1.04:analytical chem | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.04:analytical chem | Radiant Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.04:analytical chem | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| 1.04:analytical chem | RH % | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.04:analytical chem | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.04:analytical chem | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.04:analytical chem | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.04:analytical chem | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.05:general inst lab | 1.05:general inst lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.05:general inst lab | RH % | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.05:general inst lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.05:general inst lab | Plug Load Electricity | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.05:general inst lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.05:general inst lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.06:water quality lab | 1.06:water quality lab | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.06:water quality lab | RH % | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.06:water quality lab | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.06:water quality lab | Plug Load Electricity | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.06:water quality lab | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.06:water quality lab | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.07:Office Prep | 1.07:Office Prep | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.07:Office Prep | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.07:Office Prep | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.07:Office Prep | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.07:Office Prep | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.08:kitchen | 1.08:kitchen | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.08:kitchen | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.08:kitchen | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.08:kitchen | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.08:kitchen | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.09:reading room | 1.09:reading room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.09:reading room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.09:reading room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.09:reading room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.09:reading room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| 1.09:reading room | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.10:Corridor | 1.10:Corridor | Temp | 1 | 1 Minute |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
| 1.10:Corridor | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.10:Corridor | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.10:Corridor | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.10:Corridor | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.11:Hall3.4 | 1.11:Hall3.4 | Temp | 1 | 1 Minute |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
| 1.11:Hall3.4 | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.11:Hall3.4 | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.11:Hall3.4 | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.11:Hall3.4 | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.12:MotheringArea | 1.12:MotheringArea | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.12:MotheringArea | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.12:MotheringArea | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.12:MotheringArea | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.12:MotheringArea | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.13First Aid | 1.13First Aid | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.13First Aid | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.13First Aid | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.13First Aid | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.13First Aid | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.14Cleaners Store | 1.14Cleaners Store | Temp | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.14Cleaners Store | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.14Cleaners Store | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.14Cleaners Store | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.14Cleaners Store | Door/Window Open Signal | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.15CleanRoom | 1.15CleanRoom | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.15CleanRoom | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.15CleanRoom | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.15CleanRoom | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.15CleanRoom | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.16:Ch Room | 1.16:Ch Room |  | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.16:Ch Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.16:Ch Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.16:Ch Room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.16:Ch Room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.17:ICP Room | 1.17:ICP Room |  | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.17:ICP Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.17:ICP Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.17:ICP Room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.17:ICP Room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.18:weighing room | 1.18:weighing room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.18:weighing room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.18:weighing room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.18:weighing room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.18:weighing room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.19:shower | 1.19:shower | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.19:shower | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.19:shower | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.19:shower | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.19:shower | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.20:HCWC | 1.20:HCWC | Temp | 1 | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.20:HCWC | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.20:HCWC | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.20:HCWC | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.20:HCWC | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.21:open plan office left | 1.21:open plan office left | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.21:open plan office left | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.21:open plan office left | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.21:open plan office left | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.21:open plan office left | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.22:BreakoutspaceRight | 1.22:BreakoutspaceRight | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.22:BreakoutspaceRight | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.22:BreakoutspaceRight | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.22:BreakoutspaceRight | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.22:BreakoutspaceRight | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.22:BreakoutspaceRight | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.23:open plan office right | 1.23:open plan office right | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.23:open plan office right | Temp |  | 1 Minute
| 1.23:open plan office right | Temp |  | 1 Minute
| 1.23:open plan office right | Temp |  | 1 Minute
open plan office radiant | 1.23:open plan office right | Radiant Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Occupancy | 1.23:open plan office right | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Relative Humididty | 1.23:open plan office right | Relative Humidity | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.23:open plan office right | Relative Humidity |  | 1 Minute
| 1.23:open plan office right | Relative Humidity |  | 1 Minute
| 1.23:open plan office right | Relative Humidity |  | 1 Minute
| 1.23:open plan office right | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.23:open plan office right | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.23:open plan office right | Occupancy | 1 | 1 Minute |  |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| 1.23:open plan office right | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.23:open plan office right | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.23:open plan office right | Lux Sensor |  | 1 Minute
| 1.23:open plan office right | Lux Sensor |  | 1 Minute
| 1.23:open plan office right | Lux Sensor |  | 1 Minute
1.24:BreakoutSpace | 1.24:BreakoutSpace | Temp | 1 | 1 Minute |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
| 1.24:BreakoutSpace | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.24:BreakoutSpace | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.24:BreakoutSpace | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.24:BreakoutSpace | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.24:BreakoutSpace | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.24:BreakoutSpace | Relative Humidity | 1 | 1 Minute
1.25:tech support | 1.25:tech support | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.25:tech support | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.25:tech support | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.25:tech support | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.25:tech support | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.25:tech support | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.26:director | 1.26:director | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.26:director | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.26:director | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.26:director | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.26:director | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.26:director | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.27:manager | 1.27:manager | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.27:manager | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.27:manager | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.27:manager | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.27:manager | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.27:manager | Lux Sensor | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.28:Seminar Room | 1.28:Seminar Room | Temp | 1 | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| 1.28:Seminar Room | Temp |  | 1 Minute
| 1.28:Seminar Room | Temp |  | 1 Minute
| 1.28:Seminar Room | Lighting Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.28:Seminar Room | Plug Load Electricity | 1 | 1 Minute |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| 1.28:Seminar Room | Occupancy | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.28:Seminar Room | Door/Window Open Signal | 1 | 1 Minute |  |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| 1.28:Seminar Room | Relative Humidity |  | 1 Minute
| 1.28:Seminar Room | Relative Humidity |  | 1 Minute
| 1.28:Seminar Room | Relative Humidity |  | 1 Minute
| 1.28:Seminar Room | Lux Sensor |  | 1 Minute | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.28:Seminar Room | Lux Sensor |  | 1 Minute
| 1.28:Seminar Room | Lux Sensor |  | 1 Minute
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 503 |  |  | 53 | 206 | 212 | 105 | 83 | 11 | 8 | 0 | 195 | 204
[9 empty] | 20.8748 |  |  |  | NO | ok | ok
[6 empty] | Total From Tiers |  | 471

## ERI_EnergyManagerSystems
Heating/Cooling Water Meters and Sensors
Building Object | Function | Function (Unit) | Measurement Interval | Archived | Sensor/Meter Placement | Placement Constraints | Comment | Comment 2 | Required Measurements | Required Tier 1 | Required Tier 2 | Required Tier 3 | Existing Measurements | Exisiting Tier 1 | Existing Tier 2 | Existing Tier 3 | Missing Tier 1 | Missing Tier 2 | Missing Tier 3
Site | Outside | Temp | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Site | wind direction | degrees | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Site | wind speed | m/s | 1 Minute | No |  |  | Roof |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Site | Outside RH | % | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Site | Outside light | Lux | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Site | Total solar radiation | Watt | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Site | Diffuse solar radiation | Watt | 1 Minute | No |  |  | Roof |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc02 total | kWh | 1 Minute | No |  |  | This measurement is not much use | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc02 today | kWh | 1 Minute | No |  |  | Break down of these panels in Larry Swift Page 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc02 day1 | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc1 total | kWh | 1 Minute | No | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc1 today | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | mcc1 day1 | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | main power board today | kWh | 1 Minute | No | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | main power board day1 | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec |  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | Lighting meter (board 7) total | kWh | 1 Minute | No |  |  | This is not whole building Lighting | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | Lighting meter (board 7) today | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Elec | Lighting meter (board 7) day1 | kWh | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Does this include compressors and pumps | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | main power board total | kWh |  | No |  |  |  |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Cooling Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Heating Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Ventilation Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Lighting Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Plug Loads Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total People Movers Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Water Services Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Break Down of Electrical Boards | Total Compressed Air Elec | kWh | 1 Minute |  |  |  | Duplicate Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Cooling Units Electricity | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total (Could be summed or get separate totals) | Total Heat Recovered to Aquafer | kWh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Total (Could be summed or get separate totals) | Cooling Elec In | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Total (Could be summed or get separate totals) | Cooling Out Heat Meter (Flow Rate) | kWh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Total (Could be summed or get separate totals) | Flow Temp | C | 1 Minute | [5 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Total (Could be summed or get separate totals) | Return Temp | C | 1 Minute | [5 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Total (Could be summed or get separate totals) | Valve Position | % | 1 Minute | [5 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Controlled Unit Temp 0-15 | Elec In | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Unit Temp 0-16 | Cooling Out Heat Meter | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Unit Temp 0-17 | Hours of operation | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Unit Temp 0-18 | Control Signal | % | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Unit Temp 0-19 | Zone Temperature | C | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Controlled Temp Unit 10-20 | Elec In | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Temp Unit 10-21 | Cooling Out Heat Meter | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Temp Unit 10-22 | Hours of operation | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Temp Unit 10-23 | Control Signal | % | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Temp Unit 10-24 | Zone Temperature | C | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Controlled Temp Unit 15-20 | Elec In | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Temp Unit 15-21 | Cooling Out Heat Meter | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Temp Unit 15-22 | Hours of operation | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Controlled Temp Unit 15-23 | Control Signal | % | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Controlled Temp Unit 15-24 | Zone Temperature | C | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Chilled Storage Unit | Elec In | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Chilled Storage Unit | Cooling Out Heat Meter | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Chilled Storage Unit | Hours of operation | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Chilled Storage Unit | Control Signal | % | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Chilled Storage Unit | Zone Temperature | C | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Frozen Area | Elec In | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Frozen Area | Cooling Out Heat Meter | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Frozen Area | Hours of operation | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Frozen Area | Control Signal | % | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Frozen Area | Zone Temperature | C | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Include Misc Fans by adding |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Ventialtion Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Lighting | Total Lights Electrical Consumption | kWh | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Lighting | Lower Ground Floor Electrical Consumption | kWh | 1 Minute |  |  |  | Duplicate From Other Sheet | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Lighting | Ground Floor Electrical Consumption | kWh | 1 Minute |  |  |  | Duplicate From Other Sheet | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Lighting | 1st Floor Electrical Consumption | kWh | 1 Minute |  |  |  | Duplicate From Other Sheet | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Lighting | Security Lights | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Lighting | Façade Lights | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Lighting | Roof lights | kWh |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Plug Loads Electricty | Total Plug Loads Elec | kWh |  |  |  |  | Sum of Plug Loads from Other sheet |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
People Movers Electricty | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
People Movers Electricty | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Water Services Electricity | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Compressed Air | All Compressed Air Elec | kWh | [6 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Compressed Air | Nominal Meters of Air Out | M3 | [6 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Compressed Air | Elec in | kWh |  |  |  |  | Meter for individual Compressed Unit |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Compressed Air | Control Signal | % | [6 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Gas | Total Building Gas Consumption | m3 | 1Minute | [5 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Building Gas | labs total | m3 | 1 Minute | No |  |  |  | Understand these meters | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Building Gas | labs today | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Gas | labs day1 | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Gas | boilers (total) | m3 | 1 Minute | No |  |  | Duplicate Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Gas | boilers (today) | m3 | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Gas | boilers (day1) | m3 | 1 Minute | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | Mains water meter total | m3 | 1 Minute | No |  |  |  |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Building Water | Mains water meter today | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | Mains water meter day1 | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | Cold water meter total | m3 | 1 Minute | No |  |  |  |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Building Water | Cold water meter today | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | Cold water meter day1 | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | Cold Water Mains Temperature | C | 1 Minute |  |  |  |  | Duplicate Measurement | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Building Water | HW meter total | m3 | 1 Minute | No |  |  |  |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Building Water | HW meter today | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Building Water | HW meter day1 | m3 | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Total Heating Energy (Elec and Gas) | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Total Heating Gas | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Total Heating Elec | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Total Heat Output | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Elecrical Related Heat Output | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating | Gas Related Heat Output | kWh | 1 Minute |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Electricty | Total Heating | [5 empty] | This is not a single measurement, addition of others |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Heating Electricty | Aquafier/Heat Pump | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Electricty | Cooling Heat Recovery | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Electricty | Solar | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Electricty | Boiler | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Main Plant System | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | A1 (out of aquifer pumps) | Temp |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Aquifer/Heat Pump | Water Low Level | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Temp out of Solar Preheat (Not A2) | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Aquifer/Heat Pump | Aquifer Water Flow Rate Meter | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Aquifer/Heat Pump | Heat pump heat meter | kWh |  | No |  |  |  | Accurate | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Heat pump heat meter today | kWh |  | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Heat pump heat meter day-1 | kWh |  | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Incoming mains temp | Temp |  | No |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Aquifer pumps Operating Status | % |  | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Aquifer Pumps Control Signal | % | [6 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
Aquifer/Heat Pump | A2 - Combined after both preheat Inlet Temp | Temp |  | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | VA2 - valve to drain from HE1 and HE2 | Valve% |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Aquifer/Heat Pump | A3 Heat Pump Supply Side Outlet Temperature | Temp |  | No |  |  |  | Out 3 degrees | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | P01/P01/P03 Electricity Meter | kWh | 1 Minute |  |  |  |  | Duplicate | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Aquifer/Heat Pump | P01/P01/P03 Control Signal | % | 1 Minute |  |  |  |  | Duplicate | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Aquifer/Heat Pump | P01/P01/P03 Hours Run Meter | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C1 Return from HE-1 | Temp |  | No |  |  | All cooling Elec in Section Electricity Cooling' |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Cooling | C2 Inlet to HE-1 | Temp |  | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Cooling | VC5 cooling circ mix valve | % |  | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Cooling | Heat Rejected to Aquafier | kWh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Cooling | P5A/P5B Electrical Consumption | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Cooling | P5A/P5B Control Signal | % | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Cooling | P5A/P5B Hours Run | Hours | 15 Minutes | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Solar Circuit | Solar heat meter total | kWh | 1 Minute | No |  |  |  | Accurate | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Solar Circuit | Solar heat meter today | kWh | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Solar Circuit | Solar heat meter day-1 | kWh | 1 Minute | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Solar Circuit | VS1. through HE2 at 100% | % | 1 Minute | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | VS2. from HW tanks at 100 % | % | 1 Minute | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | S1 temp into panels | temp | 1 Minute | No |  |  |  | find these | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | S2 temp out of panels | temp | 1 Minute | No |  |  |  | find these | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Solar Circuit | S3 temp out of HW tanks (base) | temp | 1 Minute | No |  |  |  | find these | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | S4 temp out of evac tube | temp | 1 Minute | No |  |  |  | find these | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Solar Circuit | S5 temp out of flat plate | temp | 1 Minute | No |  |  |  | find these | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | HW2 temp in Tank CO1A | temp | 1 Minute | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | HW4 temp in Tank CO2B | temp | 1 Minute | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Solar Circuit | Tubes Heat Meter | kwh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Solar Circuit | Flat Plate Heat Meter | kwh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Solar Circuit | Solar circuit aqufier Heat Meter | kwh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Solar Circuit | P6A/P6B Electrical Consumption | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Solar Circuit | P6A/P6B Control Signal | % | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Solar Circuit | P6A/P6B Hours Run | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Solar Circuit | Heat Meter Solar to Calorifiers | kWh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
6 Separate sets of collectors/What Resolution of Measurement | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Underfloor Heating | Underfloor heat meter total | kWh |  | No |  |  |  | Accurate | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Underfloor Heating | Underfloor heat meter today | kWh |  | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Underfloor Heating | Underfloor heat meter day-1 | kWh |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Underfloor Heating | UF1 Demand Inlet heat pump | temp |  | No |  |  |  | Out 3 degrees | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Underfloor Heating | UF2 Demand Outlet heat pump | temp |  | No |  |  |  | Out 3 degrees | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Underfloor Heating | UF3 Underfloor Return Temp | temp |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Underfloor Heating | UF4 iUnderFloor Supply Temp | temp |  | No |  |  |  | Out 5 degrees | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Underfloor Heating | VUF1 Valve to Bypass Underfloor Circuit | % |  | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Underfloor Heating | P8A/P8B Electricity Meter | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Underfloor Heating | P8A/P8B Control Signal | % | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Underfloor Heating | P8A/P8B Hours Run Meter | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Boiler | Boiler Heat meter total | kWh |  | No |  |  |  | Accurate | 1 | 1 |  | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0
Boiler | Boiler Heat meter today | kWh |  | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Boiler | Boiler Heat meter day-1 | kWh |  | No |  |  | Same Measurement | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Boiler | Tank CO2 to Boiler | temp |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Boiler | VHW1 mix valve from boiler to Tank CO2 | % |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Boiler | B1 Boiler Outlet Temperature | temp |  | No |  |  |  | Out 10 degrees | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
Boiler | B1 Boiler Inlet Temperature | temp |  | No |  |  |  | Out 10 degrees | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Boiler | Boiler water to UF heating | % |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Boiler | Boiler to HE-04 Heat Meter | kWh | 1 Minute | [5 empty] | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Boiler | Boiler Hours Run Meter | Hours | 1 Minute |  |  |  | Need to have measurement on VA4/VA3 /VA1 etc.. |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Boiler | P13A/P13B Electricity Meter | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Boiler | P13A/P13B Control Signal | % | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Boiler | P13A/P13B Hours Run Meter | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Boiler | boilers (total) | m3 | 1 Minute | No |  |  |  |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Coils | Heating coils heat meter | kWh |  | No |  |  |  | Slightly Out | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Heating Coils | Heating coils heat meter today | kWh |  | No |  |  | Same Meter | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Coils | Heating coils heat meter day-1 | kWh |  | No |  |  | Same Meter | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Heating Coils | Return Temp AHU heating coils | temp |  | No |  |  |  | Out 5 degrees | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Heating Coils | Supply Temp is a duplicate | Temp |  |  |  |  | Duplicate on Boiler Object | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Storage | CO1A Temperature | Temp |  |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Storage | CO1B Temperature | Temp |  |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Storage | CO2 Temperature | Temp |  |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Storage | Cold (Mains) Water Inlet Temp | Temp |  |  |  |  | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
DHW | HW3 out of hot water to DHW | temp | 1 Minute | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
DHW | DHW Quantity Consumed | m3/s | 1 Minute | [5 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
DHW | Incoming Mains Water Temp | temp | 1 Minute | [5 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
DHW | Temp in Tank CO2 | temp | 1 Minute | No |  |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
DHW | P11A/P11B Electrical Consumption | kWh | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
DHW | P11A/P11B Control Signal | % | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
DHW | P11A/P11B Hours Run | Hours | 1 Minute | [5 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | No | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
DHW | ON |  |  | No |  |  |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 1 | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 1 | % Open | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 1 | [8 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 1 | Trip | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 1 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Wheel Electrical Energy | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Pre Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Post Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Supply Tempertaure | [7 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
AHU 1 | Duct Static Pressure | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
AHU 1 | Temperature | [5 empty] | Duplicate Measurement Zone | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 1 | Return Air RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Pressure ? | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 1 | Return Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Return Post Wheel RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 1 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 1 | Temperature | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 2 | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 2 | % Open | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 2 | [8 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 2 | Trip | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 2 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Wheel Electrical Energy | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Pre Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Post Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Supply Tempertaure | [7 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
AHU 2 | Duct Static Pressure | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
AHU 2 | Temperature | [5 empty] | Duplicate Measurement Zone | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 2 | Return Air RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Pressure ? | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 2 | Return Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Return Post Wheel RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 2 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 2 | Temperature | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 3 | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 3 | % Open | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 3 | [8 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 3 | Trip | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 3 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Wheel Electrical Energy | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Pre Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Post Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Supply Tempertaure | [7 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
AHU 3 | Duct Static Pressure | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
AHU 3 | Temperature | [5 empty] | Duplicate Measurement Zone | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 3 | Return Air RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Pressure ? | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 3 | Return Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Return Post Wheel RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 3 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 3 | Temperature | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 5 | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 5 | % Open | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 5 | [8 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 5 | Trip | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 5 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Wheel Electrical Energy | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Pre Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Post Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Supply Tempertaure | [7 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
AHU 5 | Duct Static Pressure | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
AHU 5 | Temperature | [5 empty] | Duplicate Measurement Zone | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 5 | Return Air RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Pressure ? | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 5 | Return Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Return Post Wheel RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 5 | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 5 | Temperature | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | [6 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | % Open | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | [8 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Trip | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Wheel Electrical Energy | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Pre Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Post Wheel Supply RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Post coil Air Temperture | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Heating coil Water Flow Temperature | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Heating Coil Water Return Temperature | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Heating Coil Water Flow Rate | [5 empty] | Duplicate | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Fault | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Supply Tempertaure | [7 empty] | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Duct Static Pressure | [7 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
AHU 4 (Cleanroom) | Pressure | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Temperature | [5 empty] | Duplicate Measurement Zone | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Return Air RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Local On/off Switch | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Pressure ? | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Return Post Wheel Temperature | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Return Post Wheel RH | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Command | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
AHU 4 (Cleanroom) | Fault | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Return Fan Speed | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
AHU 4 (Cleanroom) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
AHU 4 (Cleanroom) | Temperature | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Extract Fans | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
EF1.01 (Micro Fossils) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.01 (Micro Fossils) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.02 (Eco-Toxicology) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.02 (Eco-Toxicology) | Elec meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.03(Aquatic Tank Holding) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.03(Aquatic Tank Holding) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.04(Water Systems Ctl) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.04(Water Systems Ctl) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.05(Eco-Tox Incubation Units) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.05(Eco-Tox Incubation Units) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.06(X-Ray Photo Lab) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.06(X-Ray Photo Lab) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF1.07(Analytical Chemistry) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF1.07(Analytical Chemistry) | Elec Meter | [7 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
EF2.01(Mothering Area) | Enable | [6 empty] | Can I relate Run time to Zone Function | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
EF2.01(Mothering Area) | Elec Meter | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Windows | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Alarms | [8 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
[9 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1A | Temp | Degrees C | 15 Minutes |  |  | No |  |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
Atrium Windows Group No. 1 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Atrium Windows Group No. 2 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Atrium Windows Group No. 3 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Windows Group No. 4 First Floor Technical Support | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Windows Group No. 4 First Floor Technical Support | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Windows Group No. 4 First Floor Technical Support | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 5 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 6 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 7 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 6 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 7 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.6 Windows Group No. 8 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.1 Windows Group No. 7 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Open Plan Office 3.1 Windows Group No. 8 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Open Plan Office 3.1 Windows Group No. 9 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Inter-Institutional Visiting Collegiate Windows Group No. 8 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Ground Floor Inter-Institutional Visiting Collegiate Windows Group No. 9 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Inter-Institutional Visiting Collegiate Windows Group No. 10 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Open Plan Office 2.1 Windows Group No. 9 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Ground Floor Open Plan Office 2.1 Windows Group No. 10 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Open Plan Office 2.1 Windows Group No. 11 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Windows Group No. 10 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Windows Group No. 10 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Windows Group No. 10 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Open Plan office 2.2 Windows Group No. 11 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Ground Floor Open Plan office 2.2 Windows Group No. 12 | Maually Opened Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Ground Floor Open Plan office 2.2 Windows Group No. 13 | Maually Closed Signal | [7 empty] | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Smoke Vent Stairs 4 Windows Group No. 12 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
Smoke Vent Stairs 1Windows Group No. 13 | Window Open Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Fume Hoods | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total Fume Hoods |  | Addition of all others | [6 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
[9 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG23:Fume Hood A | [6 empty] | Fume Hood on Off Signal Not on BMS |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG23:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG23:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
LG24:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG24:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG24:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
LG25:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG25:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG25:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
LG26:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG26:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG26:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
LG27:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG27:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG27:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
LG28:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
LG28:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
LG28:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
G04:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
G04:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G04:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
G05:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
G05:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G05:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
G05:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
G05:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
G05:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.01:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.01:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.01:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.02:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.02:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.02:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.02:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.02:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.02:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.03:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.03:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.03:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.03:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.03:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.03:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.03:Fume Hood C | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.03:Fume Hood C | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.03:Fume Hood C | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.04:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.04:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.04:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.04:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.04:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.04:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.05:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.05:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.05:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.05:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.05:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.05:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.05:Fume Hood C | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.05:Fume Hood C | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.05:Fume Hood C | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.06:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.06:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.06:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.06:Fume Hood B | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.06:Fume Hood B | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.06:Fume Hood B | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
1.15:Fume Hood A | [8 empty] | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
1.15:Fume Hood A | [8 empty] | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
1.15:Fume Hood A | Control Signal | [7 empty] | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
[8 empty] | Total | 361 | 37 | 142 | 183 | 186 | 23 | 90 | 70 | 14 | 52 | 113
[17 empty] | ok | ok | ok
[8 empty] | Perentage of Required Measurements | 51.5235 |  | Total Tiers | 362 | % Inclusion
Existing heat meter -
New heat meter required - | [8 empty] | Total |  |  |  | Total |  |  | `
[8 empty] | Total Plant & Geometry | 864 |  |  |  | 291
Electricity meter -
[8 empty] | Total % of Required Measurements | 33.6806 |  |  |  | Total Building Percentage |  |  | Required | Existing | Missing | Percentage
Hours run meter - | [14 empty] | Total | 861 | 283 | 578 | 0.32869
[15 empty] | Tier 1 | 120 | 106 | 14 | 0.88333
[15 empty] | Tier 2 | 346 | 99 | 247 | 0.28613
[15 empty] | Tier 3 | 395 | 78 | 317 | 0.19747
Table Totals

## PrototypeLEED
Level | Building Object | Sensor/Meter Name | Measurement Description | Function (Unit) | Measurement Interval | Comment | Required Measurements | Required Tier 1 | Required Tier 2 | Required Tier 3 | Existing Measurements | Exisiting Tier 1 | Existing Tier 2 | Existing Tier 3 | Missing Tier 1 | Missing Tier 2 | Missing Tier 3
Solar Circuit | Solar Circuit | hms1 | Solar heat meter total | kWh | 1 Minute |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | hms1 | Solar heat meter today | kWh | 1 Minute | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | hms1 | Solar heat meter day-1 | kWh | 1 Minute | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | VS1 | VS1. through HE2 at 100% | % | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | VS2 | VS2. from HW tanks at 100 % | % | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S1 | S1 temp into panels | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S2 | S2 temp out of panels | temp | 1 Minute |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Solar Circuit | S3 | S3 temp out of HW tanks (base) | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S4 | S4 temp out of evac tube | temp | 1 Minute |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Solar Circuit | S5 | S5 temp out of flat plate | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | HW1 | HW2 temp in Tank CO1A | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | HW2 | HW4 temp in Tank CO2B | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit |  | Tubes Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | Flat Plate Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | Solar circuit aqufier Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | P6A/P6B Electrical Consumption | kWh | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | P6A/P6B Control Signal | % | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | P6A/P6B Hours Run | Hours | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | Heat Meter Solar to Calorifiers | kWh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
[6 empty] | Totals | 17 | 5 | 2 | 10 | 10 | 1 | 2 | 7 | 4 | 0 | 3
Solar Circuit | Solar Circuit | hms1 | Solar heat meter total | kWh | 1 Minute |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | hms1 | Solar heat meter today | kWh | 1 Minute | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | hms1 | Solar heat meter day-1 | kWh | 1 Minute | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Solar Circuit | VS1 | VS1. through HE2 at 100% | % | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | VS2 | VS2. from HW tanks at 100 % | % | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S1 | S1 temp into panels | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S2 | S2 temp out of panels | temp | 1 Minute |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Solar Circuit | S3 | S3 temp out of HW tanks (base) | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | S4 | S4 temp out of evac tube | temp | 1 Minute |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Solar Circuit | S5 | S5 temp out of flat plate | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | HW1 | HW2 temp in Tank CO1A | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit | HW2 | HW4 temp in Tank CO2B | temp | 1 Minute |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Solar Circuit |  | Tubes Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | Flat Plate Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | Solar circuit aqufier Heat Meter | kwh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
| Solar Circuit |  | P6A/P6B Electrical Consumption | kWh | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | P6A/P6B Control Signal | % | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | P6A/P6B Hours Run | Hours | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Solar Circuit |  | Heat Meter Solar to Calorifiers | kWh | 1 Minute |  | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0
Main Plant System | Main Plant System | Hot water/cooling systems | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aquifer/Heat Pump | Aquifer/Heat Pump | A1 | A1 (out of aquifer pumps) | Temp |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Aquifer/Heat Pump |  | Water Low Level |  |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump |  | Temp out of Solar Preheat (Not A2) |  |  |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Aquifer/Heat Pump |  | Aquifer Water Flow Rate Meter |  |  |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Aquifer/Heat Pump | hmuf1 | Heat pump heat meter | kWh |  |  | 1 | 1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump | hmuf1 | Heat pump heat meter today | kWh |  | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump | hmuf1 | Heat pump heat meter day-1 | kWh |  | Same Measurement | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump | Heat pump circuit | Incoming mains temp | Temp |  | Duplicate | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump | Heat pump circuit | Aquifer pumps Operating Status | % |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump |  | Aquifer Pumps Control Signal | % |  |  | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 1 | 0
| Aquifer/Heat Pump | A2 | A2 - Combined after both preheat Inlet Temp | Temp |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump | VA2 | VA2 - valve to drain from HE1 and HE2 | Valve% |  |  | 1 |  |  | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
| Aquifer/Heat Pump | A3 | A3 Heat Pump Supply Side Outlet Temperature | Temp |  |  | 1 |  | 1 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
| Aquifer/Heat Pump |  | P01/P01/P03 Electricity Meter | kWh | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Aquifer/Heat Pump |  | P01/P01/P03 Control Signal | % | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
| Aquifer/Heat Pump |  | P01/P01/P03 Hours Run Meter | Hours | 1 Minute |  | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 1
[6 empty] | Total | 30 | 6 | 9 | 15 | 17 | 2 | 6 | 9 | 4 | 3 | 6
[7 empty] | Required | Existing | Missing | Percentage
[6 empty] | Total | 30 | 17 | 13 | 0.56667
[6 empty] | Tier 1 | 6 | 2 | 4 | 0.33333
[6 empty] | Tier 2 | 9 | 6 | 3 | 0.66667
[6 empty] | Tier 3 | 15 | 9 | 6 | 0.6